## IO Assignment
Cabinet_ID | Cabinet_Type | Cabinet_Direction | Limiting_Factor | Board_ID | Board_Type | Channel_No | Relay_Required | Signal_Type | JB | I/O Type | terminal-1 | terminal-2 | Tag No | Location | IS/NIS | Loop No | Voltage | To | Marshaling | idk | card | idk2 | card1 | card2 | channel | TB | all | system | real card | card-terminal | terminal-1.1 | terminal-2.1 | SRC | IO_RAW | IO_KEY | SAFETY_RAW | LOC_RAW
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-110-006 | AI | 9 | 10 | T-110-43 | FIELD | IS | TIT-110-43 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 5 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 03-1 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-110-006 | AI | 11 | 12 | T-110-46 | FIELD | IS | TIT-110-46 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 6 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 03-2 | 7 | 8 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-110-006 | AI | 13 | 14 | T-110-49 | FIELD | IS | TIT-110-49 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 7 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 04-1 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 4 | NO | HOT_SPARE | JB-DIA-110-006 | AI | 23 | 24 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 5 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 03-1 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-110-007 | AI | 17 | 18 | P-120-15 | FIELD | IS | PDIT-120-15 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 9 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 05-1 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-110-007 | AI | 19 | 20 | P-120-83 | FIELD | IS | PIT-120-83 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 10 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 05-2 | 29 | 30 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-110-007 | AI | 21 | 22 | T-120-109 | FIELD | IS | TIT-120-109 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 11 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 06-1 | 33 | 34 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-110-007 | AI | 23 | 24 | L-120-642A | FIELD | IS | LIT-120-642A | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 12 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 06-2 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-110-007 | AI | 25 | 26 | L-120-642S | FIELD | IS | LIT-120-642S | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 13 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 07-1 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-110-007 | AI | 27 | 28 | P-120-643A | FIELD | IS | PIT-120-643A | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 14 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 07-2 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-110-007 | AI | 29 | 30 | P-120-643S | FIELD | IS | PIT-120-643S | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 15 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 08-1 | 17 | 18 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-110-007 | AI | 31 | 32 | P-120-09 | FIELD | IS | PIT-120-09 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 16 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 08-2 | 23 | 24 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 13 | NO | HOT_SPARE | JB-DIA-110-007 | AI | 33 | 34 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 9 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 05-1 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-110-008 | AI | 15 | 16 | T-120-15 | FIELD | IS | TIT-120-15 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 8 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 04-2 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-110-008 | AI | 17 | 18 | T-120-17 | FIELD | IS | TIT-120-17 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 9 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 05-1 | 17 | 18 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-01 | Barrier Board | 16 | NO | HOT_SPARE | JB-DIA-110-008 | AI | 19 | 20 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 8 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 04-2 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-450-001 | AI | 1 | 2 | L-450-612 | FIELD | IS | LIT-450-612 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 1 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 01-1 | 5 | 6 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-450-001 | AI | 3 | 4 | P-450-613 | FIELD | IS | PIT-450-613 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 2 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 01-2 | 7 | 8 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-450-002 | AI | 5 | 6 | P-450-07 | FIELD | IS | PDIT-450-07 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 3 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 02-1 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-450-002 | AI | 7 | 8 | P-450-12 | FIELD | IS | PDIT-450-12 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 4 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 02-2 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-450-002 | AI | 9 | 10 | P-450-17 | FIELD | IS | PDIT-450-17 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 5 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 03-1 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-110-006 | AIR | 13 | 14 | T-110-41 | FIELD | IS | TIT-110-41 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 7 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 04-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-110-006 | AIR | 15 | 16 | T-110-44 | FIELD | IS | TIT-110-44 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 8 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 04-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-110-006 | AIR | 17 | 18 | T-110-47 | FIELD | IS | TIT-110-47 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 9 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 05-1 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 9 | NO | HOT_SPARE | JB-DIA-110-006 | AIR | 25 | 26 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 7 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 04-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-110-007 | AIR | 11 | 12 | T-120-52 | FIELD | IS | TIT-120-52 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 6 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 03-2 | 35 | 36 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-110-007 | AIR | 19 | 20 | F-120-13 | FIELD | IS | FIT-120-13 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 10 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 05-2 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-110-007 | AIR | 21 | 22 | P-120-11 | FIELD | IS | PIT-120-11 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 11 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 06-1 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-110-007 | AIR | 23 | 24 | T-120-14 | FIELD | IS | TIT-120-14 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 12 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 06-2 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-110-007 | AIR | 25 | 26 | T-120-19 | FIELD | IS | TIT-120-19 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 13 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 07-1 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-110-007 | AIR | 27 | 28 | F-120-93 | FIELD | IS | FIT-120-93-1 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 14 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 07-2 | 21 | 22 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-02 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-110-007 | AIR | 29 | 30 | L-120-17 | FIELD | IS | LIT-120-17 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 15 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 08-1 | 27 | 28 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-110-007 | AIR | 31 | 32 | L-120-14 | FIELD | IS | LIT-120-14 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 16 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 08-2 | 31 | 32 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 2 | NO | HOT_SPARE | JB-DIA-110-007 | AIR | 35 | 36 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 6 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 03-2 | 35 | 36 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-110-008 | AIR | 5 | 6 | F-120-11 | FIELD | IS | FIT-120-11 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 3 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 02-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-110-008 | AIR | 7 | 8 | F-120-12 | FIELD | IS | FIT-120-12 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 4 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 02-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-110-008 | AIR | 9 | 10 | F-120-92 | FIELD | IS | FIT-120-92 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 5 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 03-1 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-110-008 | AIR | 11 | 12 | L-120-06 | FIELD | IS | LIT-120-06 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 6 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 03-2 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-110-008 | AIR | 13 | 14 | L-120-12 | FIELD | IS | LIT-120-12 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 7 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 04-1 | 11 | 12 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-110-008 | AIR | 15 | 16 | L-120-91 | FIELD | IS | LIT-120-91 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 8 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 04-2 | 13 | 14 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 9 | NO | HOT_SPARE | JB-DIA-110-008 | AIR | 21 | 22 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 3 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 02-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-450-002 | AIR | 1 | 2 | L-450-02 | FIELD | IS | LIT-450-02 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 1 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 01-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-450-002 | AIR | 3 | 4 | L-450-13 | FIELD | IS | LIT-450-13 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 2 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 01-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-450-002 | AIR | 5 | 6 | L-450-18 | FIELD | IS | LIT-450-18 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 3 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 02-1 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-450-002 | AIR | 7 | 8 | T-450-06 | FIELD | IS | TIT-450-06 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 4 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 02-2 | 19 | 20 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-450-002 | AIR | 9 | 10 | T-450-11 | FIELD | IS | TIT-450-11 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 5 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 03-1 | 23 | 24 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-450-002 | AIR | 11 | 12 | T-450-16 | FIELD | IS | TIT-450-16 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 6 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 03-2 | 27 | 28 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AI)-03 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-450-002 | AIR | 13 | 14 | L-450-07 | FIELD | IS | LIT-450-07 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 7 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 04-1 | 29 | 30 | SC | AIR | AIR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-110-006 | AOR | 13 | 14 | T-110-41 | FIELD | IS | TY-110-41 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 7 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 04-1 | 13 | 14 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-110-006 | AOR | 15 | 16 | T-110-44 | FIELD | IS | TY-110-44 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 8 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 04-2 | 15 | 16 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-110-006 | AOR | 17 | 18 | T-110-47 | FIELD | IS | TY-110-47 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 9 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 05-1 | 17 | 18 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-110-006 | AOR | 19 | 20 | T-120-31 | FIELD | IS | TY-120-31 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 10 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 05-2 | 19 | 20 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-110-006 | AOR | 21 | 22 | T-120-61 | FIELD | IS | TY-120-61 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 11 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 06-1 | 21 | 22 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 6 | NO | HOT_SPARE | JB-DIA-110-006 | AOR | 27 | 28 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 7 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 04-1 | 13 | 14 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-110-007 | AOR | 25 | 26 | L-120-17 | FIELD | IS | LCV-120-17 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 13 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 07-1 | 19 | 20 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-110-007 | AOR | 27 | 28 | F-120-93 | FIELD | IS | FCV-120-93 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 14 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 07-2 | 25 | 26 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 9 | NO | HOT_SPARE | JB-DIA-110-007 | AOR | 37 | 38 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 13 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 07-1 | 19 | 20 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-110-008 | AOR | 1 | 2 | F-120-11 | FIELD | IS | FCV-120-11 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 1 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 01-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-110-008 | AOR | 3 | 4 | F-120-13 | FIELD | IS | FCV-120-13 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 2 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 01-2 | 19 | 20 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-110-008 | AOR | 5 | 6 | T-120-14 | FIELD | IS | TCV-120-14 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 3 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 02-1 | 21 | 22 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 13 | NO | SPARE | JB-DIA-110-008 | AOR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 3 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 02-1 | 21 | 22 |  | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 14 | NO | SPARE | JB-DIA-110-008 | AOR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 3 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 02-1 | 21 | 22 |  | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 15 | NO | SPARE | JB-DIA-110-008 | AOR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 3 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 02-1 | 21 | 22 |  | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-01 | Barrier Board | 16 | NO | SPARE | JB-DIA-110-008 | AOR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 3 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 02-1 | 21 | 22 |  | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-110-008 | AOR | 7 | 8 | F-120-12 | FIELD | IS | FCV-120-12 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 4 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 02-2 | 23 | 24 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-110-008 | AOR | 9 | 10 | F-120-92 | FIELD | IS | FCV-120-92 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 5 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 03-1 | 25 | 26 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-110-008 | AOR | 11 | 12 | T-120-02 | FIELD | IS | TCV-120-02 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 6 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 03-2 | 27 | 28 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 4 | NO | HOT_SPARE | JB-DIA-110-008 | AOR | 23 | 24 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 1 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 01-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-450-001 | AOR | 1 | 2 | P-450-21 | FIELD | IS | PCV-450-21B | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 1 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 01-1 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-450-001 | AOR | 3 | 4 | P-450-23 | FIELD | IS | PCV-450-23 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 2 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 01-2 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-450-002 | AOR | 7 | 8 | L-450-13 | FIELD | IS | LCV-450-13 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 4 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 02-2 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-450-002 | AOR | 9 | 10 | L-450-18 | FIELD | IS | LCV-450-18 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 5 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 03-1 | 7 | 8 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-450-002 | AOR | 11 | 12 | T-450-06 | FIELD | IS | TCV-450-06 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 6 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 03-2 | 17 | 18 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-450-002 | AOR | 13 | 14 | T-450-11 | FIELD | IS | TCV-450-11 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 7 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 04-1 | 21 | 22 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-450-002 | AOR | 15 | 16 | T-450-16 | FIELD | IS | TCV-450-16 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 8 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 04-2 | 25 | 26 | SC | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 12 | NO | SPARE | JB-DIA-450-002 | AOR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 8 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 04-2 | 25 | 26 |  | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 13 | NO | SPARE | JB-DIA-450-002 | AOR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 8 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 04-2 | 25 | 26 |  | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 14 | NO | SPARE | JB-DIA-450-002 | AOR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 8 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 04-2 | 25 | 26 |  | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 15 | NO | SPARE | JB-DIA-450-002 | AOR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 8 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 04-2 | 25 | 26 |  | AOR | AOR | IS | FIELD
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Barrier Board (AO)-02 | Barrier Board | 16 | NO | SPARE | JB-DIA-450-002 | AOR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 8 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 04-2 | 25 | 26 |  | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 1 | NO | ACTIVE | HOLD-AI-PK-3193-01 | AI | 1 | 2 | - | FIELD | IS | LIT-930-520 | 4-20 MA HART | DCS | DSC-001-001F | 15 | C1-AI13 | L1-13 | AI13 | - | 1 | TB1 | DSC-001-001F.C1-AI13.TB1 /DMC-001-001R.TB-C1-AI13 | DMC-001-001R | TB-C1-AI13 | 01-1 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 2 | NO | ACTIVE | HOLD-AI-PK-3193-01 | AI | 3 | 4 | - | FIELD | IS | LIT-930-521 | 4-20 MA HART | DCS | DSC-001-001F | 15 | C1-AI13 | L1-13 | AI13 | - | 2 | TB1 | DSC-001-001F.C1-AI13.TB1 /DMC-001-001R.TB-C1-AI13 | DMC-001-001R | TB-C1-AI13 | 01-2 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 3 | NO | ACTIVE | HOLD-AI-PK-3193-01 | AI | 5 | 6 | - | FIELD | IS | LIT-930-523 | 4-20 MA HART | DCS | DSC-001-001F | 15 | C1-AI13 | L1-13 | AI13 | - | 3 | TB1 | DSC-001-001F.C1-AI13.TB1 /DMC-001-001R.TB-C1-AI13 | DMC-001-001R | TB-C1-AI13 | 02-1 | 5 | 6 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 4 | NO | ACTIVE | HOLD-AI-PK-3193-01 | AI | 7 | 8 | - | FIELD | IS | LIT-930-528 | 4-20 MA HART | DCS | DSC-001-001F | 15 | C1-AI13 | L1-13 | AI13 | - | 4 | TB1 | DSC-001-001F.C1-AI13.TB1 /DMC-001-001R.TB-C1-AI13 | DMC-001-001R | TB-C1-AI13 | 02-2 | 7 | 8 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 5 | NO | ACTIVE | HOLD-AI-PK-3193-01 | AI | 9 | 10 | - | FIELD | IS | LIT-930-529 | 4-20 MA HART | DCS | DSC-001-001F | 15 | C1-AI13 | L1-13 | AI13 | - | 5 | TB1 | DSC-001-001F.C1-AI13.TB1 /DMC-001-001R.TB-C1-AI13 | DMC-001-001R | TB-C1-AI13 | 03-1 | 9 | 10 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 6 | NO | ACTIVE | HOLD-AI-PK-3193-01 | AI | 11 | 12 | - | FIELD | IS | LIT-930-531 | 4-20 MA HART | DCS | DSC-001-001F | 15 | C1-AI13 | L1-13 | AI13 | - | 6 | TB1 | DSC-001-001F.C1-AI13.TB1 /DMC-001-001R.TB-C1-AI13 | DMC-001-001R | TB-C1-AI13 | 03-2 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 7 | NO | ACTIVE | HOLD-AI-PK-3193-01 | AI | 13 | 14 | - | FIELD | IS | LIT-930-532 | 4-20 MA HART | DCS | DSC-001-001F | 15 | C1-AI13 | L1-13 | AI13 | - | 7 | TB1 | DSC-001-001F.C1-AI13.TB1 /DMC-001-001R.TB-C1-AI13 | DMC-001-001R | TB-C1-AI13 | 04-1 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 8 | NO | ACTIVE | HOLD-AI-PK-3193-01 | AI | 15 | 16 | - | FIELD | IS | PIT-930-540 | 4-20 MA HART | DCS | DSC-001-001F | 15 | C1-AI13 | L1-13 | AI13 | - | 8 | TB1 | DSC-001-001F.C1-AI13.TB1 /DMC-001-001R.TB-C1-AI13 | DMC-001-001R | TB-C1-AI13 | 04-2 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 9 | NO | HOT_SPARE | HOLD-AI-PK-3193-01 | AI | 17 | 18 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 15 | C1-AI13 | L1-13 | AI13 | - | 1 | TB1 | DSC-001-001F.C1-AI13.TB1 /DMC-001-001R.TB-C1-AI13 | DMC-001-001R | TB-C1-AI13 | 01-1 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-100-001 | AI | 1 | 2 | F-100-14 | FIELD | IS | FIT-100-14 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 1 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 01-1 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-100-001 | AI | 3 | 4 | P-100-11 | FIELD | IS | PDIT-100-11 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 2 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 01-2 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-100-001 | AI | 5 | 6 | P-100-12 | FIELD | IS | PDIT-100-12 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 3 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 02-1 | 5 | 6 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-100-001 | AI | 7 | 8 | P-100-13 | FIELD | IS | PDIT-100-13 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 4 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 02-2 | 7 | 8 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-100-001 | AI | 9 | 10 | P-100-14 | FIELD | IS | PDIT-100-14 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 5 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 03-1 | 9 | 10 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-100-001 | AI | 11 | 12 | T-100-03 | FIELD | IS | TIT-100-03 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 6 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 03-2 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-01 | Barrier Board | 16 | NO | HOT_SPARE | JB-DIA-100-001 | AI | 13 | 14 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 1 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 01-1 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-100-002 | AI | 1 | 2 | P-100-11 | FIELD | IS | FIT-100-03 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 1 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 01-1 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-100-002 | AI | 3 | 4 | P-100-14 | FIELD | IS | PIT-100-05 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 2 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 01-2 | 9 | 10 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-100-002 | AI | 5 | 6 | L-100-04 | FIELD | IS | PIT-120-40 | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 3 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 02-1 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 4 | NO | HOT_SPARE | JB-DIA-100-002 | AI | 7 | 8 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 19 | C1-AI08 | L1-8 | AI08 | - | 1 | TB1 | DSC-001-001F.C1-AI08.TB1 /DMC-001-002R.IB-C1-AI08 | DMC-001-002R | IB-C1-AI08 | 01-1 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-110-001 | AI | 11 | 12 | P-200-03 | FIELD | IS | PDIT-200-03 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 6 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 03-2 | 9 | 10 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 6 | NO | HOT_SPARE | JB-DIA-110-001 | AI | 13 | 14 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 6 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 03-2 | 9 | 10 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-110-002 | AI | 13 | 14 | A-120-91 | FIELD | IS | AIT-120-91 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 7 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 04-1 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 8 | NO | HOT_SPARE | JB-DIA-110-002 | AI | 23 | 24 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 7 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 04-1 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-110-005 | AI | 29 | 30 | P-120-23 | FIELD | IS | PDIT-120-23 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 15 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 08-1 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-110-005 | AI | 31 | 32 | P-120-56 | FIELD | IS | PDIT-120-56 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 16 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 08-2 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 11 | NO | HOT_SPARE | JB-DIA-110-005 | AI | 33 | 34 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 15 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 08-1 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-110-009 | AI | 19 | 20 | F-120-02 | FIELD | IS | FIT-120-02 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 10 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 05-2 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 13 | NO | HOT_SPARE | JB-DIA-110-009 | AI | 25 | 26 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 10 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 05-2 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-110-011 | AI | 1 | 2 | P-110-02 | FIELD | IS | PDIT-110-02 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 1 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 01-1 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-110-011 | AI | 3 | 4 | P-110-06 | FIELD | IS | PDIT-110-06 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 2 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 01-2 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-02 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-110-011 | AI | 5 | 6 | P-110-09 | FIELD | IS | PDIT-110-09 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 3 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 02-1 | 17 | 18 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 1 | NO | HOT_SPARE | JB-DIA-110-011 | AI | 7 | 8 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 1 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 01-1 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-120-001 | AI | 9 | 10 | L-120-622A | FIELD | IS | LIT-120-622A | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 5 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 03-1 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-120-001 | AI | 11 | 12 | P-120-623A1 | FIELD | IS | PIT-120-623A1 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 6 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 03-2 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-120-001 | AI | 13 | 14 | L-120-622S | FIELD | IS | LIT-120-622S | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 7 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 04-1 | 9 | 10 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-120-001 | AI | 15 | 16 | P-120-623S1 | FIELD | IS | PIT-120-623S1 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 8 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 04-2 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 6 | NO | HOT_SPARE | JB-DIA-120-001 | AI | 17 | 18 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 5 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 03-1 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-120-003 | AI | 19 | 20 | L-120-84 | FIELD | IS | LIT-120-84 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 10 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 05-2 | 5 | 6 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-120-003 | AI | 21 | 22 | TI-120-81 | FIELD | IS | TIT-120-81 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 11 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 06-1 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-120-003 | AI | 23 | 24 | P-120-613 | FIELD | IS | PIT-120-613 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 12 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 06-2 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-120-003 | AI | 25 | 26 | T-120-611 | FIELD | IS | TIT-120-611 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 13 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 07-1 | 7 | 8 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-120-003 | AI | 27 | 28 | T-120-83 | FIELD | IS | TIT-120-83 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 14 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 07-2 | 19 | 20 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 12 | NO | HOT_SPARE | JB-DIA-120-003 | AI | 29 | 30 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 10 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 05-2 | 5 | 6 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-700-102 | AI | 31 | 32 | T-700-81 | FIELD | IS | TIT-700-81 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 16 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 08-2 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-100-001 | AIR | 1 | 2 | L-100-04 | FIELD | IS | LDIT-100-04 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 1 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 01-1 | 11 | 12 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-100-001 | AIR | 3 | 4 | L-100-02 | FIELD | IS | LIT-100-02 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 2 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 01-2 | 13 | 14 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-03 | Barrier Board | 16 | NO | HOT_SPARE | JB-DIA-100-001 | AIR | 15 | 16 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 1 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 01-1 | 11 | 12 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-100-002 | AIR | 1 | 2 | P-100-12 | FIELD | IS | FIT-100-05 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 1 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 01-1 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 2 | NO | HOT_SPARE | JB-DIA-100-002 | AIR | 9 | 10 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 1 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 01-1 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-110-001 | AIR | 1 | 2 | - | FIELD | IS | FIT-200-01A | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 1 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 01-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-110-001 | AIR | 3 | 4 | L-200-03 | FIELD | IS | LIT-200-03 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 2 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 01-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-110-001 | AIR | 5 | 6 | P-200-01 | FIELD | IS | PIT-200-01 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 3 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 02-1 | 11 | 12 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-110-001 | AIR | 7 | 8 | P-200-02 | FIELD | IS | PIT-200-02 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 4 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 02-2 | 13 | 14 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 7 | NO | HOT_SPARE | JB-DIA-110-001 | AIR | 15 | 16 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 1 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 01-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-110-002 | AIR | 11 | 12 | P-120-26 | FIELD | IS | PIT-120-26 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 6 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 03-2 | 17 | 18 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 9 | NO | HOT_SPARE | JB-DIA-110-002 | AIR | 25 | 26 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 6 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 03-2 | 17 | 18 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-110-005 | AIR | 15 | 16 | L-120-23 | FIELD | IS | LIT-120-23 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 8 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 04-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-110-005 | AIR | 17 | 18 | L-120-53 | FIELD | IS | LIT-120-53 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 9 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 05-1 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-110-005 | AIR | 19 | 20 | T-120-31 | FIELD | IS | TIT-120-31 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 10 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 05-2 | 15 | 16 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-110-005 | AIR | 21 | 22 | T-120-61 | FIELD | IS | TIT-120-61 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 11 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 06-1 | 17 | 18 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 14 | NO | HOT_SPARE | JB-DIA-110-005 | AIR | 35 | 36 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 8 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 04-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-110-009 | AIR | 19 | 20 | L-120-04 | FIELD | IS | LDIT-120-04 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 10 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 05-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-04 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-110-009 | AIR | 21 | 22 | P-120-03 | FIELD | IS | PIT-120-03 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 11 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 06-1 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-110-009 | AIR | 23 | 24 | T-120-02 | FIELD | IS | TIT-120-02 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 12 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 06-2 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 2 | NO | HOT_SPARE | JB-DIA-110-009 | AIR | 27 | 28 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 10 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 05-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-110-011 | AIR | 1 | 2 | L-110-03 | FIELD | IS | LIT-110-03 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 1 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 01-1 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-110-011 | AIR | 3 | 4 | L-110-06 | FIELD | IS | LIT-110-06 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 2 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 01-2 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-110-011 | AIR | 5 | 6 | L-110-09 | FIELD | IS | LIT-110-09 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 3 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 02-1 | 11 | 12 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 6 | NO | HOT_SPARE | JB-DIA-110-011 | AIR | 9 | 10 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 1 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 01-1 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-120-001 | AIR | 9 | 10 | F-120-81 | FIELD | IS | FIT-120-81 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 5 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 03-1 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-120-001 | AIR | 11 | 12 | F-120-83 | FIELD | IS | FIT-120-83 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 6 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 03-2 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-120-001 | AIR | 13 | 14 | P-120-623A2 | FIELD | IS | PIT-120-623A2 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 7 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 04-1 | 17 | 18 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-120-001 | AIR | 15 | 16 | P-120-623S2 | FIELD | IS | PIT-120-623S2 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 8 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 04-2 | 19 | 20 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 11 | NO | HOT_SPARE | JB-DIA-120-001 | AIR | 19 | 20 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 5 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 03-1 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-120-003 | AIR | 19 | 20 | F-120-85 | FIELD | IS | FIT-120-85 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 10 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 05-2 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-120-003 | AIR | 21 | 22 | P-100-01 | FIELD | IS | PIT-100-01 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 11 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 06-1 | 11 | 12 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-120-003 | AIR | 23 | 24 | L-120-83 | FIELD | IS | LIT-120-83 | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 12 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 06-2 | 17 | 18 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 15 | NO | HOT_SPARE | JB-DIA-120-003 | AIR | 31 | 32 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 5 | C1-AI04R | L1-4 | AI04 | AI04R | 10 | TB1 | DSC-001-001F.C1-AI04R.TB1 /DMC-001-003F.IB-C1-AI04R | DMC-001-003F | IB-C1-AI04R | 05-2 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AI)-05 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-700-102 | AIR | 13 | 14 | P-700-85 | FIELD | IS | PIT-700-85 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 7 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-100-002 | AOR | 1 | 2 | F-100-14 | FIELD | IS | FCV-100-05 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 1 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 01-1 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-100-002 | AOR | 3 | 4 | P-100-13 | FIELD | IS | HCV-100-01 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 2 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 01-2 | 7 | 8 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-100-002 | AOR | 5 | 6 | L-100-02 | FIELD | IS | LCV-100-04 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 3 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 02-1 | 13 | 14 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 4 | NO | HOT_SPARE | JB-DIA-100-002 | AOR | 11 | 12 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 1 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 01-1 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-110-001 | AOR | 1 | 2 | L-200-03 | FIELD | IS | LCV-200-03 | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 1 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 01-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-110-001 | AOR | 3 | 4 | P-200-01 | FIELD | IS | PCV-200-01 | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 2 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 01-2 | 7 | 8 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-110-001 | AOR | 5 | 6 | F-120-01A | FIELD | IS | FCV-200-01A | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 3 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 02-1 | 15 | 16 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 8 | NO | HOT_SPARE | JB-DIA-110-001 | AOR | 17 | 18 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 1 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 01-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-110-002 | AOR | 9 | 10 | L-120-91A | FIELD | IS | LCV-120-91A | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 5 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 03-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-110-002 | AOR | 11 | 12 | L-120-91B | FIELD | IS | LCV-120-91B | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 6 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 03-2 | 5 | 6 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-110-002 | AOR | 13 | 14 | P-120-03 | FIELD | IS | PCV-120-03 | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 7 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 04-1 | 7 | 8 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-110-002 | AOR | 15 | 16 | P-120-04 | FIELD | IS | PCV-120-04 | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 8 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 04-2 | 9 | 10 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-110-002 | AOR | 17 | 18 | P-120-12 | FIELD | IS | PCV-120-12 | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 9 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 05-1 | 11 | 12 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-110-002 | AOR | 19 | 20 | P-120-26 | FIELD | IS | PCV-120-26A | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 10 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 05-2 | 13 | 14 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-110-002 | AOR | 21 | 22 | P-120-26 | FIELD | IS | PCV-120-26B | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 11 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 06-1 | 15 | 16 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-01 | Barrier Board | 16 | NO | HOT_SPARE | JB-DIA-110-002 | AOR | 27 | 28 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 5 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 03-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-110-005 | AOR | 23 | 24 | L-120-23 | FIELD | IS | LCV-120-23 | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 12 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 06-2 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-110-005 | AOR | 25 | 26 | L-120-53 | FIELD | IS | LCV-120-53 | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 13 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 07-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-110-005 | AOR | 27 | 28 | P-120-11 | FIELD | IS | PCV-120-11 | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 14 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 07-2 | 9 | 10 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 4 | NO | HOT_SPARE | JB-DIA-110-005 | AOR | 37 | 38 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 9 | C1-AO03R | L1-16 | AO03 | AO03R | 12 | TB1 | DSC-001-001R.C1-AO03R.TB1 /DMC-001-001F.IB-C1-AO03R | DMC-001-001F | IB-C1-AO03R | 06-2 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-110-009 | AOR | 15 | 16 | L-120-04 | FIELD | IS | LCV-120-04 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 8 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 04-2 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 6 | NO | HOT_SPARE | JB-DIA-110-009 | AOR | 29 | 30 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 8 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 04-2 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-110-011 | AOR | 1 | 2 | L-110-03 | FIELD | IS | LCV-110-03 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 1 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 01-1 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-110-011 | AOR | 3 | 4 | L-110-06 | FIELD | IS | LCV-110-06 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 2 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 01-2 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-110-011 | AOR | 5 | 6 | L-110-09 | FIELD | IS | LCV-110-09 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 3 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 02-1 | 5 | 6 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 10 | NO | HOT_SPARE | JB-DIA-110-011 | AOR | 11 | 12 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 1 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 01-1 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-120-001 | AOR | 7 | 8 | F-120-81 | FIELD | IS | FCV-120-81 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 4 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 02-2 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-120-001 | AOR | 9 | 10 | F-120-83 | FIELD | IS | FCV-120-83 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 5 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 03-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 13 | NO | HOT_SPARE | JB-DIA-120-001 | AOR | 21 | 22 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 4 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 02-2 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-120-003 | AOR | 11 | 12 | F-120-85 | FIELD | IS | FCV-120-85 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 6 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 03-2 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-120-003 | AOR | 13 | 14 | P-100-01 | FIELD | IS | PCV-100-01 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 7 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 04-1 | 9 | 10 | SC | AOR | AOR | IS | FIELD
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | Barrier Board (AO)-02 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-700-102 | AOR | 23 | 24 | P-700-85 | FIELD | IS | PCV-700-85 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 12 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 06-2 | 5 | 6 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-010-003 | AI | 1 | 2 | PIT-001-025 | FIELD | IS | PIT-001-025 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 1 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 01-1 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-010-003 | AI | 3 | 4 | PIT-001-024 | FIELD | IS | PIT-001-024 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 2 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 01-2 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-010-003 | AI | 5 | 6 | PIT-002-036 | FIELD | IS | PIT-002-036 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 3 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 02-1 | 5 | 6 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-010-003 | AI | 7 | 8 | PIT-002-062 | FIELD | IS | PIT-002-062 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 4 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 02-2 | 7 | 8 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 5 | NO | HOT_SPARE | JB-DIA-010-003 | AI | 9 | 10 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 1 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 01-1 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-110-004 | AI | 15 | 16 | L-900-01 | FIELD | IS | LIT-900-01 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 8 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 04-2 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-110-004 | AI | 17 | 18 | P-900-02 | FIELD | IS | PIT-900-02 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 9 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 05-1 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-110-004 | AI | 19 | 20 | P-900-623 | FIELD | IS | PIT-900-623 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 10 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 05-2 | 5 | 6 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-110-004 | AI | 21 | 22 | T-900-621 | FIELD | IS | TIT-900-621 | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 11 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 06-1 | 7 | 8 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 10 | NO | HOT_SPARE | JB-DIA-110-004 | AI | 23 | 24 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 7 | C1-AI09 | L1-9 | AI09 | - | 8 | TB1 | DSC-001-001F.C1-AI09.TB1 /DMC-001-001F.IB-C1-AI09 | DMC-001-001F | IB-C1-AI09 | 04-2 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-450-003 | AI | 11 | 12 | F-450-21 | FIELD | IS | FIT-450-21 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 6 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 03-2 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-450-003 | AI | 13 | 14 | L-450-22 | FIELD | IS | LIT-450-22 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 7 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 04-1 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-450-003 | AI | 15 | 16 | T-450-118 | FIELD | IS | TIT-450-118 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 8 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 04-2 | 13 | 14 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-450-003 | AI | 17 | 18 | T-450-24 | FIELD | IS | TIT-450-24 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 9 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 05-1 | 15 | 16 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-500-002 | AI | 29 | 30 | P-500-28 | FIELD | IS | PDIT-500-28 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI10 | L1-10 | AI10 | - | 15 | TB1 | DSC-001-001F.C1-AI10.TB1 /DMC-001-003F.IB-C1-AI10 | DMC-001-003F | IB-C1-AI10 | 08-1 | 7 | 8 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-01 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-500-003 | AI | 19 | 20 | P-500-05 | FIELD | IS | PDIT-500-05 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 10 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 05-2 | 9 | 10 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-500-003 | AI | 21 | 22 | P-500-183 | FIELD | IS | PDIT-500-183 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 11 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 06-1 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-700-101 | AI | 23 | 24 | L-700-632A | FIELD | IS | LIT-700-632A1 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 12 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 06-2 | 9 | 10 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-700-101 | AI | 25 | 26 | P-700-633A1 | FIELD | IS | PIT-700-633A1 | 4-20 MA HART | DCS | DSC-001-001F | 11 | C1-AI11 | L1-11 | AI11 | - | 13 | TB1 | DSC-001-001F.C1-AI11.TB1 /DMC-001-001R.IB-C1-AI11 | DMC-001-001R | IB-C1-AI11 | 07-1 | 11 | 12 | SC | AI | AI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 4 | NO | ACTIVE | HOLD-AI05R | AIR | 21 | 22 | T-120-621S1 | FIELD | IS | TIT-120-621S1 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 11 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 06-1 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 5 | NO | ACTIVE | HOLD-AI05R | AIR | 23 | 24 | V-120-629S | FIELD | IS | VIT-120-629S | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 12 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 06-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 6 | NO | ACTIVE | HOLD-AI05R | AIR | 25 | 26 | P-120-539 | FIELD | IS | PIT-120-539 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 13 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 07-1 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 7 | NO | ACTIVE | HOLD-AI05R | AIR | 27 | 28 | IR-120-501 | FIELD | IS | IR-120-501 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 14 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 07-2 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 8 | NO | HOT_SPARE | HOLD-AI05R | AIR | 29 | 30 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 11 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 06-1 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-110-003 | AIR | 5 | 6 | F-200-02 | FIELD | IS | FIT-200-02 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 3 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 02-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-110-003 | AIR | 7 | 8 | P-110-04 | FIELD | IS | PIT-110-04 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 4 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 02-2 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-110-003 | AIR | 9 | 10 | P-200-06 | FIELD | IS | PIT-200-06 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 5 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 03-1 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 12 | NO | HOT_SPARE | JB-DIA-110-003 | AIR | 13 | 14 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI02R | L1-2 | AI02 | AI02R | 3 | TB1 | DSC-001-001F.C1-AI02R.TB1 /DMC-001-002R.IB-C1-AI02R | DMC-001-002R | IB-C1-AI02R | 02-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-110-010 | AIR | 25 | 26 | F-110-51 | FIELD | IS | FIT-110-51 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 13 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 07-1 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-110-010 | AIR | 27 | 28 | L-110-54 | FIELD | IS | LDIT-110-54 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 14 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 07-2 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-110-010 | AIR | 29 | 30 | L-110-53 | FIELD | IS | LIT-110-53 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 15 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 08-1 | 11 | 12 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-02 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-110-010 | AIR | 31 | 32 | P-110-51 | FIELD | IS | PIT-110-51 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 16 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 08-2 | 13 | 14 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 1 | NO | HOT_SPARE | JB-DIA-110-010 | AIR | 33 | 34 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI01R | L1-1 | AI01 | AI01R | 13 | TB1 | DSC-001-001F.C1-AI01R.TB1 /DMC-001-002F.IB-C1-AI01R | DMC-001-002F | IB-C1-AI01R | 07-1 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-450-003 | AIR | 15 | 16 | P-450-21 | FIELD | IS | PIT-450-21 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 8 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 04-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-450-003 | AIR | 17 | 18 | P-450-23 | FIELD | IS | PIT-450-23 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 9 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 05-1 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-450-003 | AIR | 19 | 20 | T-450-110 | FIELD | IS | TIT-450-110 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 10 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 05-2 | 11 | 12 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-500-001 | AIR | 1 | 2 | P-500-141 | FIELD | IS | PIT-500-141 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 1 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 01-1 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-500-001 | AIR | 3 | 4 | P-500-37 | FIELD | IS | PIT-500-37 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 2 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 01-2 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-500-002 | AIR | 7 | 8 | L-500-28 | FIELD | IS | LIT-500-28 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 4 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 02-2 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-500-002 | AIR | 9 | 10 | P-500-29 | FIELD | IS | PIT-500-29 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 5 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 03-1 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-500-003 | AIR | 21 | 22 | L-500-03 | FIELD | IS | LIT-500-03 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 11 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 06-1 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-500-003 | AIR | 23 | 24 | L-500-183 | FIELD | IS | LIT-500-183 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 12 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 06-2 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-700-101 | AIR | 27 | 28 | F-700-81 | FIELD | IS | FIT-700-81 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 14 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 07-2 | 5 | 6 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-700-101 | AIR | 29 | 30 | P-700-123 | FIELD | IS | PIT-700-123 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI06R | L1-6 | AI06 | AI06R | 15 | TB1 | DSC-001-001F.C1-AI06R.TB1 /DMC-001-001R.IB-C1-AI06R | DMC-001-001R | IB-C1-AI06R | 08-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-700-601 | AIR | 25 | 26 | P-700-633A2 | FIELD | IS | PIT-700-633A2 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 13 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 07-1 | 1 | 2 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-700-601 | AIR | 27 | 28 | T-700-631A1 | FIELD | IS | TIT-700-631A1 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 14 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 07-2 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-700-601 | AIR | 29 | 30 | V-700-639A1 | FIELD | IS | VIT-700-639A1 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 15 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 08-1 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AI)-03 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-700-601 | AIR | 31 | 32 | V-700-639A2 | FIELD | IS | VIT-700-639A2 | 4-20 MA HART | DCS | DSC-001-001F | 1 | C1-AI03R | L1-3 | AI03 | AI03R | 16 | TB1 | DSC-001-001F.C1-AI03R.TB1 /DMC-001-001F.IB-C1-AI03R | DMC-001-001F | IB-C1-AI03R | 08-2 | 9 | 10 | SC | AIR | AIR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-110-003 | AOR | 9 | 10 | F-200-02 | FIELD | IS | FCV-200-02 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 5 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 03-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-110-003 | AOR | 11 | 12 | P-110-04 | FIELD | IS | PCV-110-04 | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 6 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 03-2 | 5 | 6 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 3 | NO | HOT_SPARE | JB-DIA-110-003 | AOR | 15 | 16 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 5 | C1-AO02R | L1-15 | AO02 | AO02R | 5 | TB1 | DSC-001-001R.C1-AO02R.TB1 /DMC-001-002R.IB-C1-AO02R | DMC-001-002R | IB-C1-AO02R | 03-1 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-110-010 | AOR | 17 | 18 | F-110-51 | FIELD | IS | FCV-110-51 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 9 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 05-1 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 5 | NO | ACTIVE | JB-DIA-110-010 | AOR | 19 | 20 | L-110-53 | FIELD | IS | LCV-110-53 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 10 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 05-2 | 5 | 6 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-110-010 | AOR | 21 | 22 | L-110-54 | FIELD | IS | LCV-110-54 | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 11 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 06-1 | 7 | 8 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 7 | NO | HOT_SPARE | JB-DIA-110-010 | AOR | 35 | 36 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001R | 1 | C1-AO01R | L1-14 | AO01 | AO01R | 9 | TB1 | DSC-001-001R.C1-AO01R.TB1 /DMC-001-002F.IB-C1-AO01R | DMC-001-002F | IB-C1-AO01R | 05-1 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 8 | NO | ACTIVE | JB-DIA-450-003 | AOR | 19 | 20 | T-450-110 | FIELD | IS | TCV-450-110 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 10 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 05-2 | 9 | 10 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 9 | NO | ACTIVE | JB-DIA-500-001 | AOR | 15 | 16 | P-500-141 | FIELD | IS | PCV-500-141 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 8 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 04-2 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 10 | NO | ACTIVE | JB-DIA-500-001 | AOR | 17 | 18 | P-500-37 | FIELD | IS | PCV-500-37 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 9 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 05-1 | 5 | 6 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 11 | NO | ACTIVE | JB-DIA-500-002 | AOR | 19 | 20 | L-500-28 | FIELD | IS | LCV-500-28 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 10 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 05-2 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 12 | NO | ACTIVE | JB-DIA-500-002 | AOR | 21 | 22 | P-500-29 | FIELD | IS | PCV-500-29 | 4-20 MA HART | DCS | DSC-001-001R | 13 | C1-AO04R | L1-17 | AO04 | AO04R | 11 | TB1 | DSC-001-001R.C1-AO04R.TB1 /DMC-001-003F.IB-C1-AO04R | DMC-001-003F | IB-C1-AO04R | 06-1 | 5 | 6 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 13 | NO | ACTIVE | JB-DIA-500-003 | AOR | 21 | 22 | L-500-03 | FIELD | IS | LCV-500-03 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 11 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 06-1 | 1 | 2 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 14 | NO | ACTIVE | JB-DIA-500-003 | AOR | 23 | 24 | L-500-183 | FIELD | IS | LCV-500-183 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 12 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 06-2 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 15 | NO | ACTIVE | JB-DIA-700-101 | AOR | 27 | 28 | F-700-81 | FIELD | IS | FCV-700-81 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 14 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 07-2 | 3 | 4 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (AO)-01 | Barrier Board | 16 | NO | ACTIVE | JB-DIA-700-101 | AOR | 29 | 30 | P-700-123 | FIELD | IS | PCV-700-123 | 4-20 MA HART | DCS | DSC-001-001R | 17 | C1-AO05R | L1-18 | AO05 | AO05R | 15 | TB1 | DSC-001-001R.C1-AO05R.TB1 /DMC-001-001R.IB-C1-AO05R | DMC-001-001R | IB-C1-AO05R | 08-1 | 7 | 8 | SC | AOR | AOR | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 1 | NO | ACTIVE | JB-DID-010-003 | DI | 1 | 2 | - | FIELD | IS | MZSO-001-005 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 1 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 01-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 2 | NO | ACTIVE | JB-DID-010-003 | DI | 3 | 4 | - | FIELD | IS | MZSC-001-005 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 2 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 01-2 | 3 | 4 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 3 | NO | ACTIVE | JB-DID-010-003 | DI | 5 | 6 | - | FIELD | IS | MZSO-001-006 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 3 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 02-1 | 5 | 6 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 4 | NO | ACTIVE | JB-DID-010-003 | DI | 7 | 8 | - | FIELD | IS | MZSC-001-006 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 4 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 02-2 | 7 | 8 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 5 | NO | ACTIVE | JB-DID-010-003 | DI | 9 | 10 | - | FIELD | IS | MZSO-001-008 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 5 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 03-1 | 9 | 10 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 6 | NO | ACTIVE | JB-DID-010-003 | DI | 11 | 12 | - | FIELD | IS | MZSC-001-008 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 6 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 03-2 | 11 | 12 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 7 | NO | ACTIVE | JB-DID-010-003 | DI | 13 | 14 | GOV-001-012 | FIELD | IS | GZSC-001-012 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 7 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 04-1 | 13 | 14 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 8 | NO | ACTIVE | JB-DID-010-003 | DI | 15 | 16 | GOV-001-012 | FIELD | IS | GZSO-001-012 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 8 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 04-2 | 15 | 16 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 9 | NO | ACTIVE | JB-DID-010-003 | DI | 17 | 18 | TDS-001-002 | FIELD | IS | TDS-001-002 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 9 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 05-1 | 17 | 18 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 10 | NO | HOT_SPARE | JB-DID-010-003 | DI | 19 | 20 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 1 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 01-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 11 | NO | HOT_SPARE | JB-DID-010-003 | DI | 21 | 22 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 1 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 01-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 12 | NO | ACTIVE | JB-DID-010-004 | DI | 21 | 22 | MOV-002-061 | FIELD | IS | MZSO-002-061 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 11 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 06-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 13 | NO | ACTIVE | JB-DID-010-004 | DI | 23 | 24 | MOV-002-061 | FIELD | IS | MZSC-002-061 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 12 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 06-2 | 3 | 4 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 14 | NO | ACTIVE | JB-DID-010-004 | DI | 25 | 26 | MOV-002-062 | FIELD | IS | MZSO-002-062 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 13 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 07-1 | 5 | 6 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 15 | NO | ACTIVE | JB-DID-010-004 | DI | 27 | 28 | MOV-002-062 | FIELD | IS | MZSC-002-062 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 14 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 07-2 | 7 | 8 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-01 | Barrier Board | 16 | NO | ACTIVE | JB-DID-010-004 | DI | 29 | 30 | MOV-002-064 | FIELD | IS | MZSO-002-064 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 15 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 08-1 | 9 | 10 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 1 | NO | ACTIVE | JB-DID-010-004 | DI | 31 | 32 | MOV-002-064 | FIELD | IS | MZSC-002-064 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 16 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 08-2 | 11 | 12 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 2 | NO | ACTIVE | JB-DID-010-004 | DI | 1 | 2 | TDS-002-003 | FIELD | IS | TDS-002-003 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 17 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 09-1 | 13 | 14 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 3 | NO | ACTIVE | JB-DID-010-004 | DI | 3 | 4 | ZSX-001-004 | FIELD | IS | ZSX-001-004 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 18 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 09-2 | 15 | 16 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 4 | NO | ACTIVE | JB-DID-010-004 | DI | 5 | 6 | ZSX-001-005 | FIELD | IS | ZSX-001-005 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 19 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 10-1 | 17 | 18 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 5 | NO | ACTIVE | JB-DID-010-004 | DI | 7 | 8 | ZSX-002-062 | FIELD | IS | ZSX-002-062 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 20 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 10-2 | 19 | 20 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 6 | NO | ACTIVE | JB-DID-010-004 | DI | 9 | 10 | ZSX-002-065 | FIELD | IS | ZSX-002-065 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 21 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 11-1 | 21 | 22 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 7 | NO | HOT_SPARE | JB-DID-010-004 | DI | 33 | 34 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 11 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 06-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 8 | NO | HOT_SPARE | JB-DID-010-004 | DI | 35 | 36 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 11 | TB1 | DSC-001-002F.C1-DI02.TB1 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 06-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 9 | NO | ACTIVE | JB-DID-100-001 | DI | 13 | 14 | H-100-01 | FIELD | IS | HZSC-100-01 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 23 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 12-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 10 | NO | ACTIVE | JB-DID-100-001 | DI | 15 | 16 | U-100-01 | FIELD | IS | UZSC-100-01 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 24 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 12-2 | 3 | 4 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 11 | NO | ACTIVE | JB-DID-100-001 | DI | 17 | 18 | U-100-01 | FIELD | IS | UZSO-100-01 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 25 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 13-1 | 5 | 6 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 12 | NO | ACTIVE | JB-DID-100-001 | DI | 19 | 20 | U-100-07 | FIELD | IS | UZSC-100-07 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 26 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 13-2 | 7 | 8 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 13 | NO | ACTIVE | JB-DID-100-001 | DI | 21 | 22 | U-100-07 | FIELD | IS | UZSO-100-07 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 27 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 14-1 | 9 | 10 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 14 | NO | ACTIVE | JB-DID-100-001 | DI | 23 | 24 | U-100-16 | FIELD | IS | UZSC-100-16 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 28 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 14-2 | 11 | 12 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 15 | NO | ACTIVE | JB-DID-100-001 | DI | 25 | 26 | U-100-16 | FIELD | IS | UZSO-100-16 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 29 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 15-1 | 13 | 14 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-02 | Barrier Board | 16 | NO | ACTIVE | JB-DID-100-001 | DI | 27 | 28 | U-120-17 | FIELD | IS | UZSC-120-17 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 30 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 15-2 | 15 | 16 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 1 | NO | ACTIVE | JB-DID-100-001 | DI | 29 | 30 | U-120-17 | FIELD | IS | UZSO-120-17 | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 31 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 16-1 | 17 | 18 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 2 | NO | ACTIVE | JB-DID-100-001 | DI | 31 | 32 | U-120-17 | FIELD | IS | UHSH-120-17A | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 32 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 16-2 | 19 | 20 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 3 | NO | ACTIVE | JB-DID-100-001 | DI | 1 | 2 | U-120-17 | FIELD | IS | UHSL-120-17A | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 1 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 01-1 | 21 | 22 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 4 | NO | HOT_SPARE | JB-DID-100-001 | DI | 33 | 34 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 23 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 12-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 5 | NO | HOT_SPARE | JB-DID-100-001 | DI | 35 | 36 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 5 | C1-DI02 | L2-2 | DI02 | - | 23 | TB2 | DSC-001-002F.C1-DI02.TB2 /DMC-001-003R.IB-C1-DI02 | DMC-001-003R | IB-C1-DI02 | 12-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 6 | NO | ACTIVE | JB-DID-110-002 | DI | 15 | 16 | U-900-02 | FIELD | IS | UZSC-900-02 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 8 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 04-2 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 7 | NO | ACTIVE | JB-DID-110-002 | DI | 17 | 18 | U-900-02 | FIELD | IS | UZSO-900-02 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 9 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 05-1 | 3 | 4 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 8 | NO | ACTIVE | JB-DID-110-002 | DI | 19 | 20 | U-900-02 | FIELD | IS | UHSH-900-02A | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 10 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 05-2 | 5 | 6 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 9 | NO | ACTIVE | JB-DID-110-002 | DI | 21 | 22 | U-900-02 | FIELD | IS | UHSL-900-02A | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 11 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 06-1 | 7 | 8 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 10 | NO | ACTIVE | JB-DID-110-002 | DI | 23 | 24 | U-900-03 | FIELD | IS | UZSC-900-03 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 12 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 06-2 | 9 | 10 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 11 | NO | ACTIVE | JB-DID-110-002 | DI | 25 | 26 | U-900-03 | FIELD | IS | UZSO-900-03 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 13 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 07-1 | 11 | 12 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 12 | NO | ACTIVE | JB-DID-110-002 | DI | 27 | 28 | U-900-03 | FIELD | IS | UHSH-900-03A | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 14 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 07-2 | 13 | 14 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 13 | NO | ACTIVE | JB-DID-110-002 | DI | 29 | 30 | U-900-03 | FIELD | IS | UHSL-900-03A | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 15 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 08-1 | 15 | 16 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 14 | NO | ACTIVE | JB-DID-110-002 | DI | 31 | 32 | A-120-91 | FIELD | IS | ASL-120-91 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 16 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 08-2 | 17 | 18 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 15 | NO | ACTIVE | JB-DID-110-002 | DI | 1 | 2 | A-120-91 | FIELD | IS | AXA-120-91 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 17 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 09-1 | 19 | 20 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-03 | Barrier Board | 16 | NO | SPARE | JB-DID-110-002 | DI |  |  | SPARE | FIELD | IS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 17 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 09-1 | 19 | 20 |  | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 1 | NO | HOT_SPARE | JB-DID-110-002 | DI | 33 | 34 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 8 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 04-2 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 2 | NO | ACTIVE | JB-DID-450-001 | DI | 11 | 12 | U-450-01 | FIELD | IS | UZSC-450-01 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 22 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 11-2 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 3 | NO | ACTIVE | JB-DID-450-001 | DI | 13 | 14 | U-450-01 | FIELD | IS | UZSO-450-01 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 23 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 12-1 | 3 | 4 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 4 | NO | ACTIVE | JB-DID-450-001 | DI | 15 | 16 | U-450-02 | FIELD | IS | UZSC-450-02 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 24 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 12-2 | 5 | 6 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 5 | NO | ACTIVE | JB-DID-450-001 | DI | 17 | 18 | U-450-02 | FIELD | IS | UZSO-450-02 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 25 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 13-1 | 7 | 8 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 6 | NO | ACTIVE | JB-DID-450-001 | DI | 19 | 20 | U-450-03 | FIELD | IS | UZSC-450-03 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 26 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 13-2 | 9 | 10 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 7 | NO | ACTIVE | JB-DID-450-001 | DI | 21 | 22 | U-450-03 | FIELD | IS | UZSO-450-03 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 27 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 14-1 | 11 | 12 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 8 | NO | ACTIVE | JB-DID-450-001 | DI | 23 | 24 | U-450-04 | FIELD | IS | UZSC-450-04 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 28 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 14-2 | 13 | 14 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 9 | NO | ACTIVE | JB-DID-450-001 | DI | 25 | 26 | U-450-04 | FIELD | IS | UZSO-450-04 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 29 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 15-1 | 15 | 16 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 10 | NO | HOT_SPARE | JB-DID-450-001 | DI | 27 | 28 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 22 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 11-2 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 11 | NO | ACTIVE | JB-DID-450-002 | DI | 31 | 32 | U-450-111 | FIELD | IS | UZSC-450-111 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 32 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 16-2 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 12 | NO | ACTIVE | JB-DID-450-002 | DI | 1 | 2 | U-450-111 | FIELD | IS | UZSO-450-111 | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 1 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 01-1 | 3 | 4 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 13 | NO | ACTIVE | JB-DID-450-002 | DI | 3 | 4 | U-450-112 | FIELD | IS | UZSC-450-112 | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 2 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 01-2 | 5 | 6 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 14 | NO | ACTIVE | JB-DID-450-002 | DI | 5 | 6 | U-450-112 | FIELD | IS | UZSO-450-112 | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 3 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 02-1 | 7 | 8 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 15 | NO | HOT_SPARE | JB-DID-450-002 | DI | 33 | 34 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 32 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 16-2 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | Barrier Board (DI)-04 | Barrier Board | 16 | NO | SPARE | JB-DID-450-002 | DI |  |  | SPARE | FIELD | IS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 32 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 16-2 | 1 | 2 |  | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 1 | NO | ACTIVE | JB-DIA-700-602 | AI | 23 | 24 | T-700-631A2 | FIELD | IS | TIT-700-631A2 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 12 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 06-2 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 2 | NO | ACTIVE | JB-DIA-700-602 | AI | 25 | 26 | T-700-631A3 | FIELD | IS | TIT-700-631A3 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 13 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 07-1 | 3 | 4 | SC | AI | AI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 3 | NO | ACTIVE | JB-DIA-700-602 | AI | 27 | 28 | T-700-631A4 | FIELD | IS | TIT-700-631A4 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 14 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 07-2 | 5 | 6 | SC | AI | AI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 4 | NO | ACTIVE | JB-DIA-700-602 | AI | 29 | 30 | T-700-631A5 | FIELD | IS | TIT-700-631A5 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 15 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 08-1 | 7 | 8 | SC | AI | AI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 5 | NO | ACTIVE | LIT-002-001 | AI | 21 | 22 | LIT-002-001 | FIELD | IS | LIT-002-001 | 4-20 MA HART | DCS | DSC-001-001F | 17 | C1-AI07 | L1-7 | AI07 | - | 11 | TB1 | DSC-001-001F.C1-AI07.TB1 /DMC-001-002F.IB-C1-AI07 | DMC-001-002F | IB-C1-AI07 | 06-1 | 1 | 2 | SC | AI | AI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 6 | NO | ACTIVE | JB-DIA-120-602A | AIR | 15 | 16 | T-120-621A1 | FIELD | IS | TIT-120-621A1 | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 7 | NO | ACTIVE | JB-DIA-120-602A | AIR | 17 | 18 | V-120-629A | FIELD | IS | VIT-120-629A | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 9 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 05-1 | 7 | 8 | SC | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 8 | NO | HOT_SPARE | JB-DIA-120-602A | AIR | 19 | 20 | HOT_SPARE | FIELD | IS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 | SC | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 9 | NO | SPARE | JB-DIA-120-602A | AIR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 |  | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 10 | NO | SPARE | JB-DIA-120-602A | AIR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 |  | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 11 | NO | SPARE | JB-DIA-120-602A | AIR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 |  | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 12 | NO | SPARE | JB-DIA-120-602A | AIR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 |  | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 13 | NO | SPARE | JB-DIA-120-602A | AIR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 |  | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 14 | NO | SPARE | JB-DIA-120-602A | AIR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 |  | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 15 | NO | SPARE | JB-DIA-120-602A | AIR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 |  | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (AI)-01 | Barrier Board | 16 | NO | SPARE | JB-DIA-120-602A | AIR |  |  | SPARE | FIELD | IS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 9 | C1-AI05R | L1-5 | AI05 | AI05R | 8 | TB1 | DSC-001-001F.C1-AI05R.TB1 /DMC-001-003F.IB-C1-AI05R | DMC-001-003F | IB-C1-AI05R | 04-2 | 3 | 4 |  | AIR | AIR | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 1 | NO | ACTIVE | JB-DID-110-001 | DI | 7 | 8 | U-200-07 | FIELD | IS | UZSC-200-07 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 4 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 02-2 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 2 | NO | ACTIVE | JB-DID-110-001 | DI | 9 | 10 | U-200-07 | FIELD | IS | UZSO-200-07 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 5 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 03-1 | 3 | 4 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 3 | NO | HOT_SPARE | JB-DID-110-001 | DI | 11 | 12 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 4 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 02-2 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 4 | NO | HOT_SPARE | JB-DID-110-001 | DI | 13 | 14 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 4 | TB1 | DSC-001-002F.C1-DI03.TB1 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 02-2 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 5 | NO | ACTIVE | JB-DID-120-001 | DI | 5 | 6 | UV-002-001 | FIELD | IS | UZSC-002-001 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 19 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 10-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 6 | NO | ACTIVE | JB-DID-120-001 | DI | 7 | 8 | UV-002-001 | FIELD | IS | UZSO-002-001 | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 20 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 10-2 | 3 | 4 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 7 | NO | HOT_SPARE | JB-DID-120-001 | DI | 9 | 10 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 8 | C1-DI03 | L2-3 | DI03 | - | 19 | TB2 | DSC-001-002F.C1-DI03.TB2 /DMC-001-003R.IB-C1-DI03 | DMC-001-003R | IB-C1-DI03 | 10-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 8 | NO | ACTIVE | JB-DID-700-101 | DI | 11 | 12 | U-700-81 | FIELD | IS | UHSH-700-81A | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 6 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 03-2 | 5 | 6 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 9 | NO | ACTIVE | JB-DID-700-101 | DI | 13 | 14 | U-700-81 | FIELD | IS | UHSL-700-81A | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 7 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 04-1 | 7 | 8 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 10 | NO | ACTIVE | JB-DID-700-101 | DI | 15 | 16 | U-700-81 | FIELD | IS | UZSO-700-81 | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 8 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 04-2 | 3 | 4 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 11 | NO | ACTIVE | JB-DID-700-101 | DI | 17 | 18 | U-700-81 | FIELD | IS | UZSC-700-81 | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 9 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 05-1 | 1 | 2 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 12 | NO | HOT_SPARE | JB-DID-700-101 | DI | 19 | 20 | HOT_SPARE | FIELD | IS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 6 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 03-2 | 5 | 6 | - | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 13 | NO | SPARE | JB-DID-700-101 | DI |  |  | SPARE | FIELD | IS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 6 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 03-2 | 5 | 6 |  | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 14 | NO | SPARE | JB-DID-700-101 | DI |  |  | SPARE | FIELD | IS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 6 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 03-2 | 5 | 6 |  | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 15 | NO | SPARE | JB-DID-700-101 | DI |  |  | SPARE | FIELD | IS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 6 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 03-2 | 5 | 6 |  | DI | DI | IS | FIELD
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | Barrier Board (DI)-01 | Barrier Board | 16 | NO | SPARE | JB-DID-700-101 | DI |  |  | SPARE | FIELD | IS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 11 | C1-DI04 | L2-4 | DI04 | - | 6 | TB1 | DSC-001-002F.C1-DI04.TB1 /DMC-001-003R.IB-C1-DI04 | DMC-001-003R | IB-C1-DI04 | 03-2 | 5 | 6 |  | DI | DI | IS | FIELD
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 1 | NO | ACTIVE | INTERNAL FAULT | DI | 1A | 1B | - | FIELD | NIS | DMC1-01-FAF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 1 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 |  | 1 | 2 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 2 | NO | ACTIVE | INTERNAL FAULT | DI | 2A | 2B | - | FIELD | NIS | DMC1-01-PWF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 2 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 3 | 4 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 3 | NO | ACTIVE | INTERNAL FAULT | DI | 3A | 3B | - | FIELD | NIS | DMC1-01-ERF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 3 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 5 | 6 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 4 | NO | ACTIVE | INTERNAL FAULT | DI | 4A | 4B | - | FIELD | NIS | DMC1-01-THF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 4 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 7 | 8 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 5 | NO | ACTIVE | INTERNAL FAULT | DI | 5A | 5B | - | FIELD | NIS | DMC1-01-DRF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 5 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 9 | 10 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 6 | NO | ACTIVE | INTERNAL FAULT | DI | 11A | 11B | - | FIELD | NIS | DMC1-05-FAF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 11 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 11 | 12 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 7 | NO | ACTIVE | INTERNAL FAULT | DI | 12A | 12B | - | FIELD | NIS | DMC1-05-THF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 12 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 13 | 14 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 8 | NO | ACTIVE | INTERNAL FAULT | DI | 13A | 13B | - | FIELD | NIS | DMC1-05-DRF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 13 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 15 | 16 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 9 | NO | ACTIVE | INTERNAL FAULT | DI | 14A | 14B | - | FIELD | NIS | DSC1-01-FAF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 14 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 17 | 18 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 10 | NO | ACTIVE | INTERNAL FAULT | DI | 15A | 15B | - | FIELD | NIS | DSC1-01-PWF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 15 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 19 | 20 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 11 | NO | ACTIVE | INTERNAL FAULT | DI | 16A | 16B | - | FIELD | NIS | DSC1-01-ERF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 16 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 21 | 22 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 12 | NO | ACTIVE | INTERNAL FAULT | DI | 1A | 1B | - | FIELD | NIS | DSC1-01-THF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 17 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 23 | 24 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 13 | NO | ACTIVE | INTERNAL FAULT | DI | 2A | 2B | - | FIELD | NIS | DSC1-01-DRF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 18 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 25 | 26 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 14 | NO | ACTIVE | INTERNAL FAULT | DI | 3A | 3B | - | FIELD | NIS | GNC1-01-FAF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 19 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 27 | 28 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 15 | NO | ACTIVE | INTERNAL FAULT | DI | 4A | 4B | - | FIELD | NIS | GNC1-01-PWF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 20 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 29 | 30 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-01 | Terminal Board | 16 | NO | ACTIVE | INTERNAL FAULT | DI | 5A | 5B | - | FIELD | NIS | GNC1-01-THF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 21 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 31 | 32 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 1 | NO | ACTIVE | INTERNAL FAULT | DI | 6A | 6B | - | FIELD | NIS | GNC1-01-DRF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 22 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 33 | 34 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 2 | NO | ACTIVE | INTERNAL FAULT | DI | 7A | 7B | - | FIELD | NIS | GPC1-01-FAF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 23 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 35 | 36 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 3 | NO | ACTIVE | INTERNAL FAULT | DI | 8A | 8B | - | FIELD | NIS | GPC1-01-THF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 24 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 37 | 38 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 4 | NO | ACTIVE | INTERNAL FAULT | DI | 9A | 9B | - | FIELD | NIS | GPC1-01-DRF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 25 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 39 | 40 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 5 | NO | ACTIVE | INTERNAL FAULT | DI | 10A | 10B | - | FIELD | NIS | GPC1-01-ERF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 26 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 41 | 42 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 6 | NO | ACTIVE | INTERNAL FAULT | DI | 11A | 11B | - | FIELD | NIS | GPC1-02-FAF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 27 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 43 | 44 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 7 | NO | ACTIVE | INTERNAL FAULT | DI | 12A | 12B | - | FIELD | NIS | GPC1-02-THF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 28 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 45 | 46 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 8 | NO | ACTIVE | INTERNAL FAULT | DI | 13A | 13B | - | FIELD | NIS | GPC1-02-DRF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 29 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 47 | 48 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 9 | NO | ACTIVE | INTERNAL FAULT | DI | 14A | 14B | - | FIELD | NIS | GPC1-02-ERF | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 30 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 49 | 50 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 10 | NO | HOT_SPARE | INTERNAL FAULT | DI | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 1 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 |  | 1 | 2 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 11 | NO | HOT_SPARE | INTERNAL FAULT | DI | T3 | T4 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 1 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 |  | 1 | 2 | - | DI | DI | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 12 | NO | ACTIVE | DI15-HOLD-01 | DI | 1A | 1B | P-120-531 | LCP | NIS | PAL-120-531 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 1 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 13 | NO | ACTIVE | DI15-HOLD-01 | DI | 2A | 2B | X-120-532 | LCP | NIS | PDAH-120-532 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 2 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 3 | 4 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 14 | NO | ACTIVE | DI15-HOLD-01 | DI | 3A | 3B | X-120-530 | LCP | NIS | XA-120-531 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 3 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 5 | 6 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 15 | NO | ACTIVE | DI15-HOLD-01 | DI | 4A | 4B | X-120-536 | LCP | NIS | XA-120-536 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 4 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 7 | 8 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-02 | Terminal Board | 16 | NO | ACTIVE | DI15-HOLD-01 | DI | 5A | 5B | X-120-534 | LCP | NIS | XA-120-533 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 5 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 9 | 10 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 1 | NO | ACTIVE | DI15-HOLD-01 | DI | 6A | 6B | X-120-534 | LCP | NIS | XA-120-535 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 6 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 11 | 12 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 2 | NO | ACTIVE | DI15-HOLD-01 | DI | 8A | 8B | - | LCP | NIS | XA-120-534 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 8 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 15 | 16 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 3 | NO | HOT_SPARE | DI15-HOLD-01 | DI | T1 | T2 | HOT_SPARE | LCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 1 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 4 | NO | ACTIVE | DI15-HOLD-02 | DI | 14A | 14B | X-120-534 | LCP | NIS | FI-120-537 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 30 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 3 | 4 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 5 | NO | HOT_SPARE | DI15-HOLD-02 | DI | T1 | T2 | HOT_SPARE | LCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 30 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 3 | 4 | - | DI | DI | NIS | LCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 6 | NO | ACTIVE | XA-110-502A | DI | 13A | 13B | X-110-502A | UCP | NIS | XA-110-502A | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 13 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 7 | NO | HOT_SPARE | XA-110-502A | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 13 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 8 | NO | ACTIVE | XA-110-502B | DI | 14A | 14B | X-110-502B | UCP | NIS | XA-110-502B | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 14 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 9 | NO | HOT_SPARE | XA-110-502B | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 14 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 10 | NO | ACTIVE | IF-PDP-003 | DIR | 13A | 13B | - | FIELD | NIS | GPC1-03-FAF | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 29 | TB2 | DSC-001-002F.C1-DI01R.TB2 /DMC-001-004R.TB-C1-DI01R-2 | DMC-001-004R | TB-C1-DI01R-2 | - | 1 | 2 | - | DIR | DIR | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 11 | NO | ACTIVE | IF-PDP-003 | DIR | 14A | 14B | - | FIELD | NIS | GPC1-03-THF | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 30 | TB2 | DSC-001-002F.C1-DI01R.TB2 /DMC-001-004R.TB-C1-DI01R-2 | DMC-001-004R | TB-C1-DI01R-2 | - | 3 | 4 | - | DIR | DIR | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 12 | NO | ACTIVE | IF-PDP-003 | DIR | 15A | 15B | - | FIELD | NIS | GPC1-03-DRF | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 31 | TB2 | DSC-001-002F.C1-DI01R.TB2 /DMC-001-004R.TB-C1-DI01R-2 | DMC-001-004R | TB-C1-DI01R-2 | - | 5 | 6 | - | DIR | DIR | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 13 | NO | ACTIVE | IF-PDP-003 | DIR | 16A | 16B | - | FIELD | NIS | GPC1-03-ERF | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 32 | TB2 | DSC-001-002F.C1-DI01R.TB2 /DMC-001-004R.TB-C1-DI01R-2 | DMC-001-004R | TB-C1-DI01R-2 | - | 7 | 8 | - | DIR | DIR | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 14 | NO | HOT_SPARE | IF-PDP-003 | DIR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 29 | TB2 | DSC-001-002F.C1-DI01R.TB2 /DMC-001-004R.TB-C1-DI01R-2 | DMC-001-004R | TB-C1-DI01R-2 | - | 1 | 2 | - | DIR | DIR | NIS | -
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 15 | NO | ACTIVE | I-120-532-1 | DIR | 1A | 1B | X-120-532 | UCP | NIS | I-120-532-1 | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 1 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 | - | DIR | DIR | NIS | UCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DI)-03 | Terminal Board | 16 | NO | HOT_SPARE | I-120-532-1 | DIR | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 1 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 | - | DIR | DIR | NIS | UCP
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 1 | NO | ACTIVE | SV-930-531 | DOR | 8A | 8C | - | FIELD | NIS | SV-930-531 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 24 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 2 | NO | HOT_SPARE | SV-930-531 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 24 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 3 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 7A | 7C | X-120-87 | MCC | NIS | XSH-120-87 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 7 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 4 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 8A | 8C | X-120-87 | MCC | NIS | XSL-120-87 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 8 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 5 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 9A | 9C | X-120-88 | MCC | NIS | XSH-120-88A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 9 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 6 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 10A | 10C | X-120-88 | MCC | NIS | XSL-120-88A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 10 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 7 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 11A | 11C | X-120-623A | MCC | NIS | XSH-120-623A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 11 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 8 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 12A | 12C | X-120-623A | MCC | NIS | XSL-120-623A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 12 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 9 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 13A | 13C | X-120-622A | MCC | NIS | XSH-120-622A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 13 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 10 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 14A | 14C | X-120-622A | MCC | NIS | XSL-120-622A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 14 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 15A | 15C | X-120-98 | MCC | NIS | XSH-120-98S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 15 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 17 | 18 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-120-008 | DOR | 16A | 16C | X-120-98 | MCC | NIS | XSL-120-98S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 16 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 19 | 20 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 13 | NO | HOT_SPARE | MC-DM-IRP-120-008 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 7 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 14 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 4A | 4C | X-500-34 | MCC | NIS | XSH-500-34-3 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 4 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 15 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 5A | 5C | X-500-34 | MCC | NIS | XSL-500-34-3 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 5 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-01 | Terminal Board | 16 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 6A | 6C | X-500-194 | MCC | NIS | XSH-500-194-3 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 6 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 1 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 7A | 7C | X-500-194 | MCC | NIS | XSL-500-194-3 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 7 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 2 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 8A | 8C | X-500-204 | MCC | NIS | XSH-500-204-3 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 8 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 3 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 9A | 9C | X-500-204 | MCC | NIS | XSL-500-204-3 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 9 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 4 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 10A | 10C | X-500-07 | MCC | NIS | XSH-500-07-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 10 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 5 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 11A | 11C | X-500-07 | MCC | NIS | XSL-500-07-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 11 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 6 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 12A | 12C | X-500-17 | MCC | NIS | XSH-500-17-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 12 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 17 | 18 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 7 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 13A | 13C | X-500-17 | MCC | NIS | XSL-500-17-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 13 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 19 | 20 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 8 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 14A | 14C | X-500-34 | MCC | NIS | XSH-500-34-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 14 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 21 | 22 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 9 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 15A | 15C | X-500-34 | MCC | NIS | XSL-500-34-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 15 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 23 | 24 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 10 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 16A | 16C | X-500-44 | MCC | NIS | XSH-500-44-2 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 16 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 25 | 26 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 1A | 1C | X-500-44 | MCC | NIS | XSL-500-44-2 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 17 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 27 | 28 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 2A | 2C | X-500-194 | MCC | NIS | XSH-500-194-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 18 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 29 | 30 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 13 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 3A | 3C | X-500-194 | MCC | NIS | XSL-500-194-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 19 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 31 | 32 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 14 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 4A | 4C | X-500-204 | MCC | NIS | XSH-500-204-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 20 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 33 | 34 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 15 | NO | ACTIVE | MC-DM-IRP-500-006 | DOR | 5A | 5C | X-500-204 | MCC | NIS | XSL-500-204-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 21 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 35 | 36 | - | DOR | DOR | NIS | MCC
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | Terminal Board (DO)-02 | Terminal Board | 16 | NO | HOT_SPARE | MC-DM-IRP-500-006 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 4 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 1 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 1A | 1B | - | MCC | NIS | XA-930-511S | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 1 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 |  | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 2 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 2A | 2B | - | MCC | NIS | XL-930-511S | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 2 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 3 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 3A | 3B | - | MCC | NIS | XLP-930-511S | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 3 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 4 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 4A | 4B | - | MCC | NIS | XXL-930-511S | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 4 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 5 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 5A | 5B | - | MCC | NIS | XA-930-528 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 5 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 6 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 6A | 6B | - | MCC | NIS | XL-930-528 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 6 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 7 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 7A | 7B | - | MCC | NIS | XLP-930-528 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 7 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 8 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 8A | 8B | - | MCC | NIS | XXL-930-528 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 8 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 9 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 9A | 9B | - | MCC | NIS | XA-930-532A | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 9 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 10 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 10A | 10B | - | MCC | NIS | XL-930-532A | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 10 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 11 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 11A | 11B | - | MCC | NIS | XLP-930-532A | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 11 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 12 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 12A | 12B | - | MCC | NIS | XXL-930-532A | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 12 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 13 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 13A | 13B | - | MCC | NIS | XA-930-532S | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 13 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 14 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 14A | 14B | - | MCC | NIS | XL-930-532S | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 14 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 15 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 15A | 15B | - | MCC | NIS | XLP-930-532S | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 15 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 16 | YES | ACTIVE | HOLD-DI-PK-3193 | DI | 16A | 16B | - | MCC | NIS | XXL-930-532S | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 16 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 1 | YES | HOT_SPARE | HOLD-DI-PK-3193 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 1 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 |  | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 2 | YES | HOT_SPARE | HOLD-DI-PK-3193 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DI17 | L2-17 | DI17 | - | 1 | TB1 | DSC-001-002R.C1-DI17.TB1 /DMC-001-005R.TB-C1-DI17-1 | DMC-001-005R | TB-C1-DI17-1 |  | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 15A | 15B | X-120-61 | MCC | NIS | XA-120-61-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 31 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 16A | 16B | X-120-61 | MCC | NIS | XL-120-61-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 32 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 1A | 1B | X-120-61 | MCC | NIS | XLP-120-61-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 1 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 2A | 2B | X-120-61 | MCC | NIS | XXL-120-61-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 2 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 3A | 3B | X-120-31 | MCC | NIS | XA-120-31-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 3 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 4A | 4B | X-120-31 | MCC | NIS | XL-120-31-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 4 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 5A | 5B | X-120-31 | MCC | NIS | XLP-120-31-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 5 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 6A | 6B | X-120-31 | MCC | NIS | XXL-120-31-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 6 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 7A | 7B | X-120-50 | MCC | NIS | XA-120-50-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 7 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 8A | 8B | X-120-50 | MCC | NIS | XL-120-50-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 8 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 9A | 9B | X-120-50 | MCC | NIS | XLP-120-50-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 9 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 10A | 10B | X-120-50 | MCC | NIS | XXL-120-50-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 10 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 11A | 11B | X-120-52 | MCC | NIS | XA-120-52A | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 11 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 12A | 12B | X-120-52 | MCC | NIS | XL-120-52-A | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 12 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 13A | 13B | X-120-52 | MCC | NIS | XLP-120-52-A | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 13 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-120-001 | DI | 14A | 14B | X-120-52 | MCC | NIS | XXL-120-52-A | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 14 | TB1 | DSC-001-002F.C1-DI06.TB1 /DMC-001-005F.TB-C1-DI06-1 | DMC-001-005F | TB-C1-DI06-1 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 3 | YES | HOT_SPARE | MC-DM-IRP-120-001 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 31 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 4 | YES | HOT_SPARE | MC-DM-IRP-120-001 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 31 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 1A | 1B | X-120-61 | MCC | NIS | XA-120-61-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 17 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 2A | 2B | X-120-61 | MCC | NIS | XL-120-61-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 18 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 3A | 3B | X-120-61 | MCC | NIS | XLP-120-61-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 19 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 4A | 4B | X-120-61 | MCC | NIS | XXL-120-61-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 20 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 5A | 5B | X-120-31 | MCC | NIS | XA-120-31-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 21 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 6A | 6B | X-120-31 | MCC | NIS | XL-120-31-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 22 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 7A | 7B | X-120-31 | MCC | NIS | XLP-120-31-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 23 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 8A | 8B | X-120-31 | MCC | NIS | XXL-120-31-2 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 24 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 9A | 9B | X-120-50 | MCC | NIS | XA-120-50-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 25 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 10A | 10B | X-120-50 | MCC | NIS | XL-120-50-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 26 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 11A | 11B | X-120-50 | MCC | NIS | XLP-120-50-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 27 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 12A | 12B | X-120-50 | MCC | NIS | XXL-120-50-1 | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 28 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 13A | 13B | X-120-52 | MCC | NIS | XA-120-52-S | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 29 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 14A | 14B | X-120-52 | MCC | NIS | XL-120-52-S | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 30 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 15A | 15B | X-120-52 | MCC | NIS | XLP-120-52-S | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 31 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-120-002 | DI | 16A | 16B | X-120-52 | MCC | NIS | XXL-120-52-S | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 32 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 5 | YES | HOT_SPARE | MC-DM-IRP-120-002 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 17 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 6 | YES | HOT_SPARE | MC-DM-IRP-120-002 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 17 | C1-DI06 | L2-6 | DI06 | - | 17 | TB2 | DSC-001-002F.C1-DI06.TB2 /DMC-001-005F.TB-C1-DI06-2 | DMC-001-005F | TB-C1-DI06-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 1A | 1B | X-120-87 | MCC | NIS | XA-120-87 | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 1 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 2A | 2B | X-120-87 | MCC | NIS | XL-120-87 | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 2 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 3A | 3B | X-120-87 | MCC | NIS | XLP-120-87 | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 3 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 4A | 4B | X-120-87 | MCC | NIS | XXL-120-87 | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 4 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 5A | 5B | X-120-88 | MCC | NIS | XA-120-88A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 5 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 6A | 6B | X-120-88 | MCC | NIS | XL-120-88A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 6 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 7A | 7B | X-120-88 | MCC | NIS | XLP-120-88A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 7 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 8A | 8B | X-120-88 | MCC | NIS | XXL-120-88A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 8 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 9A | 9B | X-120-623A | MCC | NIS | XA-120-623A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 9 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 10A | 10B | X-120-623A | MCC | NIS | XL-120-623A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 10 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 11A | 11B | X-120-623A | MCC | NIS | XLP-120-623A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 11 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 12A | 12B | X-120-623A | MCC | NIS | XXL-120-623A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 12 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 13A | 13B | X-120-622A | MCC | NIS | XA-120-622A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 13 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 14A | 14B | X-120-622A | MCC | NIS | XL-120-622A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 14 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 15A | 15B | X-120-622A | MCC | NIS | XLP-120-622A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 15 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-120-005 | DI | 16A | 16B | X-120-622A | MCC | NIS | XXL-120-622A | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 16 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 7 | YES | HOT_SPARE | MC-DM-IRP-120-005 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 1 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 8 | YES | HOT_SPARE | MC-DM-IRP-120-005 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 1 | TB1 | DSC-001-002F.C1-DI07.TB1 /DMC-001-006F.TB-C1-DI07-1 | DMC-001-006F | TB-C1-DI07-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-120-006 | DI | 3A | 3B | X-120-98 | MCC | NIS | XA-120-98S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 19 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-120-006 | DI | 4A | 4B | X-120-98 | MCC | NIS | XL-120-98S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 20 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-120-006 | DI | 5A | 5B | X-120-98 | MCC | NIS | XLP-120-98S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 21 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-120-006 | DI | 6A | 6B | X-120-98 | MCC | NIS | XXL-120-98S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 22 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 13 | YES | HOT_SPARE | MC-DM-IRP-120-006 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 19 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 14 | YES | HOT_SPARE | MC-DM-IRP-120-006 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 19 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 9A | 9B | X-120-88 | MCC | NIS | XA-120-88S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 25 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 10A | 10B | X-120-88 | MCC | NIS | XL-120-88S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 26 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 11A | 11B | X-120-88 | MCC | NIS | XLP-120-88S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 27 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 12A | 12B | X-120-88 | MCC | NIS | XXL-120-88S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 28 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 13A | 13B | X-120-623S | MCC | NIS | XA-120-623S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 29 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 14A | 14B | X-120-623S | MCC | NIS | XL-120-623S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 30 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 15A | 15B | X-120-623S | MCC | NIS | XLP-120-623S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 31 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 16A | 16B | X-120-623S | MCC | NIS | XXL-120-623S | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 32 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 1A | 1B | X-120-622S | MCC | NIS | XA-120-622S | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 1 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 2A | 2B | X-120-622S | MCC | NIS | XL-120-622S | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 2 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 3A | 3B | X-120-622S | MCC | NIS | XLP-120-622S | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 3 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 4A | 4B | X-120-622S | MCC | NIS | XXL-120-622S | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 4 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 5A | 5B | P-3112-04A | MCC | NIS | XA-120-98 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 5 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 6A | 6B | X-120-98 | MCC | NIS | XL-120-98A | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 6 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 7A | 7B | X-120-98 | MCC | NIS | XLP-120-98A | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 7 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-120-007 | DI | 8A | 8B | X-120-98 | MCC | NIS | XXL-120-98A | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 8 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 15 | YES | HOT_SPARE | MC-DM-IRP-120-007 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 25 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 16 | YES | HOT_SPARE | MC-DM-IRP-120-007 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 1 | C1-DI07 | L2-7 | DI07 | - | 25 | TB2 | DSC-001-002F.C1-DI07.TB2 /DMC-001-006F.TB-C1-DI07-2 | DMC-001-006F | TB-C1-DI07-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 1 | YES | ACTIVE | XA-110-502S | DI | 15A | 15B | X-110-502S | UCP | NIS | XA-110-502S | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 15 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 2 | YES | HOT_SPARE | XA-110-502S | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 15 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 3 | YES | ACTIVE | XA-120-532 | DI | 16A | 16B | X-120-532 | UCP | NIS | XA-120-532 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 16 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 4 | YES | HOT_SPARE | XA-120-532 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 16 | TB1 | DSC-001-002F.C1-DI15.TB1 /DMC-001-004R.TB-C1-DI15-1 | DMC-001-004R | TB-C1-DI15-1 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 5 | YES | ACTIVE | XA-120-541 | DI | 1A | 1B | X-120-541 | UCP | NIS | XA-120-541 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 17 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 6 | YES | HOT_SPARE | XA-120-541 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 17 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 7 | YES | ACTIVE | XA-120-561 | DI | 2A | 2B | X-120-561 | UCP | NIS | XA-120-561 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 18 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 8 | YES | HOT_SPARE | XA-120-561 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 18 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 9 | YES | ACTIVE | XA-120-571 | DI | 3A | 3B | X-120-571 | UCP | NIS | XA-120-571 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 19 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 10 | YES | HOT_SPARE | XA-120-571 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 19 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 11 | YES | ACTIVE | XA-450-532 | DI | 4A | 4B | X-450-532 | UCP | NIS | XA-450-532 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 20 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 12 | YES | HOT_SPARE | XA-450-532 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 20 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 13 | YES | ACTIVE | XA-450-552 | DI | 5A | 5B | X-450-552 | UCP | NIS | XA-450-552 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 21 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 14 | YES | HOT_SPARE | XA-450-552 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 21 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 15 | YES | ACTIVE | XA-450-572 | DI | 6A | 6B | X-450-572 | UCP | NIS | XA-450-572 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 22 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 16 | YES | HOT_SPARE | XA-450-572 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 22 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 11A | 11B | X-450-21 | MCC | NIS | XA-450-21-3 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 11 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 12A | 12B | X-450-21 | MCC | NIS | XL-450-21-3 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 12 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 13A | 13B | X-450-21 | MCC | NIS | XLP-450-21-3 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 13 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 14A | 14B | X-450-21 | MCC | NIS | XXL-450-21-3 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 14 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 15A | 15B | X-450-21 | MCC | NIS | XA-450-21-5 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 15 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 16A | 16B | X-450-21 | MCC | NIS | XL-450-21-5 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 16 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 1A | 1B | X-450-21 | MCC | NIS | XLP-450-21-5 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 17 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 2A | 2B | X-450-21 | MCC | NIS | XXL-450-21-5 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 18 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 3A | 3B | X-450-21 | MCC | NIS | XA-450-21-7 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 19 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 4A | 4B | X-450-21 | MCC | NIS | XL-450-21-7 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 20 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 5A | 5B | X-450-21 | MCC | NIS | XLP-450-21-7 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 21 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 6A | 6B | X-450-21 | MCC | NIS | XXL-450-21-7 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 22 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 7A | 7B | X-450-21 | MCC | NIS | XA-450-21-9 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 23 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 8A | 8B | X-450-21 | MCC | NIS | XL-450-21-9 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 24 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 9A | 9B | X-450-21 | MCC | NIS | XLP-450-21-9 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 25 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-01 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-450-001 | DI | 10A | 10B | X-450-21 | MCC | NIS | XXL-450-21-9 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 26 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 1 | YES | HOT_SPARE | MC-DM-IRP-450-001 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 11 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 2 | YES | HOT_SPARE | MC-DM-IRP-450-001 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 11 | TB1 | DSC-001-002F.C1-DI08.TB1 /DMC-001-006F.TB-C1-DI08-1 | DMC-001-006F | TB-C1-DI08-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 13A | 13B | X-450-21 | MCC | NIS | XA-450-21-1 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 29 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 14A | 14B | X-450-21 | MCC | NIS | XL-450-21-1 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 30 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 15A | 15B | X-450-21 | MCC | NIS | XLP-450-21-1 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 31 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 16A | 16B | X-450-21 | MCC | NIS | XXL-450-21-1 | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 32 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 1A | 1B | X-450-21 | MCC | NIS | XA-450-21-11 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 1 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 2A | 2B | X-450-21 | MCC | NIS | XL-450-21-11 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 2 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 3A | 3B | X-450-21 | MCC | NIS | XLP-450-21-11 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 3 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 4A | 4B | X-450-21 | MCC | NIS | XXL-450-21-11 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 4 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 5A | 5B | X-450-21 | MCC | NIS | XA-450-21-13 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 5 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 6A | 6B | X-450-21 | MCC | NIS | XL-450-21-13 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 6 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 7A | 7B | X-450-21 | MCC | NIS | XLP-450-21-13 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 7 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 8A | 8B | X-450-21 | MCC | NIS | XXL-450-21-13 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 8 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 9A | 9B | X-450-21 | MCC | NIS | XA-450-21-15 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 9 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-02 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 10A | 10B | X-450-21 | MCC | NIS | XL-450-21-15 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 10 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 11A | 11B | X-450-21 | MCC | NIS | XLP-450-21-15 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 11 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-450-002 | DI | 12A | 12B | X-450-21 | MCC | NIS | XXL-450-21-15 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 12 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 3 | YES | HOT_SPARE | MC-DM-IRP-450-002 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 29 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 4 | YES | HOT_SPARE | MC-DM-IRP-450-002 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 4 | C1-DI08 | L2-8 | DI08 | - | 29 | TB2 | DSC-001-002F.C1-DI08.TB2 /DMC-001-006F.TB-C1-DI08-2 | DMC-001-006F | TB-C1-DI08-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 15A | 15B | X-450-21 | MCC | NIS | XA-450-21-4 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 15 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 16A | 16B | X-450-21 | MCC | NIS | XL-450-21-4 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 16 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 1A | 1B | X-450-21 | MCC | NIS | XLP-450-21-4 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 17 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 2A | 2B | X-450-21 | MCC | NIS | XXL-450-21-4 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 18 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 3A | 3B | X-450-21 | MCC | NIS | XA-450-21-6 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 19 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 4A | 4B | X-450-21 | MCC | NIS | XL-450-21-6 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 20 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 5A | 5B | X-450-21 | MCC | NIS | XLP-450-21-6 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 21 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 6A | 6B | X-450-21 | MCC | NIS | XXL-450-21-6 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 22 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 7A | 7B | X-450-21 | MCC | NIS | XA-450-21-8 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 23 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 8A | 8B | X-450-21 | MCC | NIS | XL-450-21-8 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 24 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 9A | 9B | X-450-21 | MCC | NIS | XLP-450-21-8 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 25 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-03 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 10A | 10B | X-450-21 | MCC | NIS | XXL-450-21-8 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 26 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 11A | 11B | X-450-21 | MCC | NIS | XA-450-21-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 27 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 12A | 12B | X-450-21 | MCC | NIS | XL-450-21-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 28 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 13A | 13B | X-450-21 | MCC | NIS | XLP-450-21-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 29 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-450-003 | DI | 14A | 14B | X-450-21 | MCC | NIS | XXL-450-21-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 30 | TB2 | DSC-001-002F.C1-DI09.TB2 /DMC-001-006F.TB-C1-DI09-2 | DMC-001-006F | TB-C1-DI09-2 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 5 | YES | HOT_SPARE | MC-DM-IRP-450-003 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 15 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 6 | YES | HOT_SPARE | MC-DM-IRP-450-003 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI09 | L2-9 | DI09 | - | 15 | TB1 | DSC-001-002F.C1-DI09.TB1 /DMC-001-006F.TB-C1-DI09-1 | DMC-001-006F | TB-C1-DI09-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 1A | 1B | X-450-21 | MCC | NIS | XA-450-21-10 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 1 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 2A | 2B | X-450-21 | MCC | NIS | XL-450-21-10 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 2 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 3A | 3B | X-450-21 | MCC | NIS | XLP-450-21-10 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 3 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 4A | 4B | X-450-21 | MCC | NIS | XXL-450-21-10 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 4 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 5A | 5B | X-450-21 | MCC | NIS | XA-450-21-12 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 5 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 6A | 6B | X-450-21 | MCC | NIS | XL-450-21-12 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 6 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 7A | 7B | X-450-21 | MCC | NIS | XLP-450-21-12 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 7 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 8A | 8B | X-450-21 | MCC | NIS | XXL-450-21-12 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 8 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 9A | 9B | X-450-21 | MCC | NIS | XA-450-21-14 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 9 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-04 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 10A | 10B | X-450-21 | MCC | NIS | XL-450-21-14 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 10 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 11A | 11B | X-450-21 | MCC | NIS | XLP-450-21-14 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 11 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 12A | 12B | X-450-21 | MCC | NIS | XXL-450-21-14 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 12 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 13A | 13B | X-450-21 | MCC | NIS | XA-450-21-16 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 13 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 14A | 14B | X-450-21 | MCC | NIS | XL-450-21-16 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 14 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 15A | 15B | X-450-21 | MCC | NIS | XLP-450-21-16 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 15 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-450-004 | DI | 16A | 16B | X-450-21 | MCC | NIS | XXL-450-21-16 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 16 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 7 | YES | HOT_SPARE | MC-DM-IRP-450-004 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 1 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 8 | YES | HOT_SPARE | MC-DM-IRP-450-004 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 1 | TB1 | DSC-001-002F.C1-DI10.TB1 /DMC-001-006R.TB-C1-DI10-1 | DMC-001-006R | TB-C1-DI10-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-450-007 | DI | 4A | 4B | X-450-22 | MCC | NIS | XA-450-22 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 20 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-450-007 | DI | 5A | 5B | X-450-22 | MCC | NIS | XL-450-22 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 21 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-450-007 | DI | 6A | 6B | X-450-22 | MCC | NIS | XLP-450-22 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 22 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-450-007 | DI | 7A | 7B | X-450-22 | MCC | NIS | XXL-450-22 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 23 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 13 | YES | HOT_SPARE | MC-DM-IRP-450-007 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 20 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 14 | YES | HOT_SPARE | MC-DM-IRP-450-007 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 20 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 13A | 13B | X-500-07 | MCC | NIS | XA-500-07-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 13 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-05 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 14A | 14B | X-500-07 | MCC | NIS | XL-500-07-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 14 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 15A | 15B | X-500-07 | MCC | NIS | XLP-500-07-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 15 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 16A | 16B | X-500-07 | MCC | NIS | XXL-500-07-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 16 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 1A | 1B | X-500-17 | MCC | NIS | XA-500-17-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 17 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 2A | 2B | X-500-17 | MCC | NIS | XL-500-17-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 18 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 3A | 3B | X-500-17 | MCC | NIS | XLP-500-17-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 19 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 4A | 4B | X-500-17 | MCC | NIS | XXL-500-17-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 20 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 5A | 5B | X-500-34 | MCC | NIS | XA-500-34-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 21 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 6A | 6B | X-500-34 | MCC | NIS | XL-500-34-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 22 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 7A | 7B | X-500-34 | MCC | NIS | XLP-500-34-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 23 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 8A | 8B | X-500-34 | MCC | NIS | XXL-500-34-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 24 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 9A | 9B | X-500-44 | MCC | NIS | XA-500-44-2 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 25 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 10A | 10B | X-500-44 | MCC | NIS | XL-500-44-2 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 26 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 11A | 11B | X-500-44 | MCC | NIS | XLP-500-44-2 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 27 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-500-002 | DI | 12A | 12B | X-500-44 | MCC | NIS | XXL-500-44-2 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 28 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 15 | YES | HOT_SPARE | MC-DM-IRP-500-002 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 13 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-06 | Terminal Board | 16 | YES | HOT_SPARE | MC-DM-IRP-500-002 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 13 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 1 | YES | ACTIVE | XA-500-513 | DI | 7A | 7B | X-500-513 | UCP | NIS | XA-500-513 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 23 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 2 | YES | HOT_SPARE | XA-500-513 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 23 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 3 | YES | ACTIVE | XA-500-518 | DI | 8A | 8B | X-500-518 | UCP | NIS | XA-500-518 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 24 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 4 | YES | HOT_SPARE | XA-500-518 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 24 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 5 | YES | ACTIVE | XA-500-523 | DI | 9A | 9B | X-500-523 | UCP | NIS | XA-500-523 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 25 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 6 | YES | HOT_SPARE | XA-500-523 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 25 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 7 | YES | ACTIVE | XA-500-527 | DI | 10A | 10B | X-500-528 | UCP | NIS | XA-500-527 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 26 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 8 | YES | HOT_SPARE | XA-500-527 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 26 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 9 | YES | ACTIVE | XA-500-533 | DI | 11A | 11B | X-500-533 | UCP | NIS | XA-500-533 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 27 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 10 | YES | HOT_SPARE | XA-500-533 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 27 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 11 | YES | ACTIVE | XA-500-537 | DI | 12A | 12B | X-500-538 | UCP | NIS | XA-500-537 | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 28 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 12 | YES | HOT_SPARE | XA-500-537 | DI | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 13 | C1-DI15 | L2-15 | DI15 | - | 28 | TB2 | DSC-001-002F.C1-DI15.TB2 /DMC-001-004R.TB-C1-DI15-2 | DMC-001-004R | TB-C1-DI15-2 | - | 1 | 2 | - | DI | DI | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 13 | YES | ACTIVE | I-120-532-2 | DIR | 2A | 2B | X-120-532 | UCP | NIS | I-120-532-2 | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 2 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 | - | DIR | DIR | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 14 | YES | ACTIVE | I-120-541-1 | DIR | 3A | 3B | X-120-541 | UCP | NIS | I-120-541-1 | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 3 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 | - | DIR | DIR | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 15 | YES | ACTIVE | I-120-541-2 | DIR | 4A | 4B | X-120-541 | UCP | NIS | I-120-541-2 | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 4 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 | - | DIR | DIR | NIS | UCP
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | Terminal Board (DI)-07 | Terminal Board | 16 | YES | ACTIVE | I-120-561-1 | DIR | 5A | 5B | X-120-561 | UCP | NIS | I-120-561-1 | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 5 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 | - | DIR | DIR | NIS | UCP
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 1A | 1B | X-110-41 | MCC | NIS | XA-110-41-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 1 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 2A | 2B | X-110-41 | MCC | NIS | XL-110-41-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 2 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 3A | 3B | X-110-41 | MCC | NIS | XLP-110-41-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 3 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 4A | 4B | X-110-41 | MCC | NIS | XXL-110-41-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 4 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 5A | 5B | X-110-44 | MCC | NIS | XA-110-44-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 5 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 6A | 6B | X-110-44 | MCC | NIS | XL-110-44-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 6 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 7A | 7B | X-110-44 | MCC | NIS | XLP-110-44-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 7 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 8A | 8B | X-110-44 | MCC | NIS | XXL-110-44-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 8 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 9A | 9B | X-110-47 | MCC | NIS | XA-110-47-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 9 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 10A | 10B | X-110-47 | MCC | NIS | XL-110-47-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 10 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 11A | 11B | X-110-47 | MCC | NIS | XLP-110-47-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 11 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-110-001 | DI | 12A | 12B | X-110-47 | MCC | NIS | XXL-110-47-1 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 12 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 13 | YES | HOT_SPARE | MC-DM-IRP-110-001 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 1 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 14 | YES | HOT_SPARE | MC-DM-IRP-110-001 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 1 | TB1 | DSC-001-002F.C1-DI05.TB1 /DMC-001-005F.TB-C1-DI05-1 | DMC-001-005F | TB-C1-DI05-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 11A | 11B | X-500-44 | MCC | NIS | XA-500-44-3 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 11 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-01 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 12A | 12B | X-500-44 | MCC | NIS | XL-500-44-3 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 12 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 13A | 13B | X-500-44 | MCC | NIS | XLP-500-44-3 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 13 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 14A | 14B | X-500-44 | MCC | NIS | XXL-500-44-3 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 14 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 15A | 15B | X-500-07 | MCC | NIS | XA-500-07-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 15 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 16A | 16B | X-500-07 | MCC | NIS | XL-500-07-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 16 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 1A | 1B | X-500-07 | MCC | NIS | XLP-500-07-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 17 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 2A | 2B | X-500-07 | MCC | NIS | XXL-500-07-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 18 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 3A | 3B | X-500-17 | MCC | NIS | XA-500-17-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 19 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 4A | 4B | X-500-17 | MCC | NIS | XL-500-17-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 20 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 5A | 5B | X-500-17 | MCC | NIS | XLP-500-17-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 21 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 6A | 6B | X-500-17 | MCC | NIS | XXL-500-17-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 22 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 7A | 7B | X-500-34 | MCC | NIS | XA-500-34-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 23 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 8A | 8B | X-500-34 | MCC | NIS | XL-500-34-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 24 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 9A | 9B | X-500-34 | MCC | NIS | XLP-500-34-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 25 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-500-004 | DI | 10A | 10B | X-500-34 | MCC | NIS | XXL-500-34-2 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 26 | TB2 | DSC-001-002F.C1-DI12.TB2 /DMC-001-006R.TB-C1-DI12-2 | DMC-001-006R | TB-C1-DI12-2 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 15 | YES | HOT_SPARE | MC-DM-IRP-500-004 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 11 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DI)-02 | Terminal Board | 16 | YES | HOT_SPARE | MC-DM-IRP-500-004 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 11 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 1 | NO | ACTIVE | JB-DNS-100-001 | DOR | 4A | 4C | U-100-01 | FIELD | NIS | UY-100-01 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 4 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 2 | NO | ACTIVE | JB-DNS-100-001 | DOR | 5A | 5C | U-100-07 | FIELD | NIS | UY-100-07 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 5 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 3 | 4 | - | DOR | DOR | NIS | FIELD
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 3 | NO | ACTIVE | JB-DNS-100-001 | DOR | 6A | 6C | U-100-16 | FIELD | NIS | UY-100-16 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 6 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 5 | 6 | - | DOR | DOR | NIS | FIELD
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 4 | NO | ACTIVE | JB-DNS-100-001 | DOR | 7A | 7C | U-120-17 | FIELD | NIS | UY-120-17 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 7 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 7 | 8 | - | DOR | DOR | NIS | FIELD
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 5 | NO | HOT_SPARE | JB-DNS-100-001 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 4 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 6 | NO | HOT_SPARE | JB-DNS-100-001 | DOR | T3 | T4 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 4 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 7 | NO | ACTIVE | HOLD-DO-PK-3193 | DOR | 9A | 9C | - | MCC | NIS | XSH-930-511S | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 25 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 8 | NO | ACTIVE | HOLD-DO-PK-3193 | DOR | 10A | 10C | - | MCC | NIS | XSL-930-511S | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 26 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 9 | NO | ACTIVE | HOLD-DO-PK-3193 | DOR | 3A | 3C | - | MCC | NIS | XSH-930-528 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 3 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 10 | NO | ACTIVE | HOLD-DO-PK-3193 | DOR | 4A | 4C | - | MCC | NIS | XSL-930-528 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 4 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 11 | NO | ACTIVE | HOLD-DO-PK-3193 | DOR | 5A | 5C | - | MCC | NIS | XSH-930-532A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 5 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 12 | NO | ACTIVE | HOLD-DO-PK-3193 | DOR | 6A | 6C | - | MCC | NIS | XSL-930-532A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 6 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 13 | NO | ACTIVE | HOLD-DO-PK-3193 | DOR | 1A | 1C | - | MCC | NIS | XSH-930-532S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 17 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 14 | NO | ACTIVE | HOLD-DO-PK-3193 | DOR | 2A | 2C | - | MCC | NIS | XSL-930-532S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 18 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 15 | NO | HOT_SPARE | HOLD-DO-PK-3193 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 25 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-01 | Terminal Board | 16 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 15A | 15C | X-450-21 | MCC | NIS | XSH-450-21-3 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 31 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 1 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 16A | 16C | X-450-21 | MCC | NIS | XSL-450-21-3 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 32 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 2 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 1A | 1C | X-450-21 | MCC | NIS | XSH-450-21-5 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 1 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 3 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 2A | 2C | X-450-21 | MCC | NIS | XSL-450-21-5 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 2 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 4 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 3A | 3C | X-450-21 | MCC | NIS | XSH-450-21-7 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 3 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 5 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 4A | 4C | X-450-21 | MCC | NIS | XSL-450-21-7 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 4 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 6 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 5A | 5C | X-450-21 | MCC | NIS | XSH-450-21-9 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 5 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 7 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 6A | 6C | X-450-21 | MCC | NIS | XSL-450-21-9 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 6 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 8 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 7A | 7C | X-450-21 | MCC | NIS | XSH-450-21-1 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 7 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 17 | 18 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 9 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 8A | 8C | X-450-21 | MCC | NIS | XSL-450-21-1 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 8 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 19 | 20 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 10 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 9A | 9C | X-450-21 | MCC | NIS | XSH-450-21-11 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 9 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 21 | 22 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 10A | 10C | X-450-21 | MCC | NIS | XSL-450-21-11 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 10 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 23 | 24 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 11A | 11C | X-450-21 | MCC | NIS | XSH-450-21-13 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 11 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 25 | 26 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 13 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 12A | 12C | X-450-21 | MCC | NIS | XSL-450-21-13 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 12 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 27 | 28 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 14 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 13A | 13C | X-450-21 | MCC | NIS | XSH-450-21-15 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 13 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 29 | 30 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 15 | NO | ACTIVE | MC-DM-IRP-450-005 | DOR | 14A | 14C | X-450-21 | MCC | NIS | XSL-450-21-15 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 14 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 31 | 32 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-02 | Terminal Board | 16 | NO | HOT_SPARE | MC-DM-IRP-450-005 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 31 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 1 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 16A | 16C | X-450-21 | MCC | NIS | XSH-450-21-4 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 16 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 2 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 1A | 1C | X-450-21 | MCC | NIS | XSL-450-21-4 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 17 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 3 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 2A | 2C | X-450-21 | MCC | NIS | XSH-450-21-6 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 18 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 4 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 3A | 3C | X-450-21 | MCC | NIS | XSL-450-21-6 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 19 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 5 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 4A | 4C | X-450-21 | MCC | NIS | XSH-450-21-8 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 20 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 6 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 5A | 5C | X-450-21 | MCC | NIS | XSL-450-21-8 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 21 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 7 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 6A | 6C | X-450-21 | MCC | NIS | XSH-450-21-2 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 22 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 8 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 7A | 7C | X-450-21 | MCC | NIS | XSL-450-21-2 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 23 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 9 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 8A | 8C | X-450-21 | MCC | NIS | XSH-450-21-10 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 24 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 17 | 18 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 10 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 9A | 9C | X-450-21 | MCC | NIS | XSL-450-21-10 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 25 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 19 | 20 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 10A | 10C | X-450-21 | MCC | NIS | XSH-450-21-12 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 26 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 21 | 22 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 11A | 11C | X-450-21 | MCC | NIS | XSL-450-21-12 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 27 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 23 | 24 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 13 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 12A | 12C | X-450-21 | MCC | NIS | XSH-450-21-14 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 28 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 25 | 26 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 14 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 13A | 13C | X-450-21 | MCC | NIS | XSL-450-21-14 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 29 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 27 | 28 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 15 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 14A | 14C | X-450-21 | MCC | NIS | XSH-450-21-16 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 30 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 29 | 30 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-03 | Terminal Board | 16 | NO | ACTIVE | MC-DM-IRP-450-006 | DOR | 15A | 15C | X-450-21 | MCC | NIS | XSL-450-21-16 | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 31 | TB2 | DSC-001-002R.C1-DO04R.TB2 /DMC-001-005R.TB-C1-DO04R-1 | DMC-001-005R | TB-C1-DO04R-1 | - | 31 | 32 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 1 | NO | HOT_SPARE | MC-DM-IRP-450-006 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 13 | C1-DO04R | L2-21 | DO04 | DO04R | 16 | TB1 | DSC-001-002R.C1-DO04R.TB1 /DMC-001-005R.TB-C1-DO04R-2 | DMC-001-005R | TB-C1-DO04R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 2 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 7A | 7C | X-500-44 | MCC | NIS | XSH-500-44-3 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 23 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 3 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 9A | 9C | X-500-07 | MCC | NIS | XSL-500-44-3 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 25 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 4 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 10A | 10C | X-500-07 | MCC | NIS | XSH-500-07-2 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 26 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 5 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 11A | 11C | X-500-17 | MCC | NIS | XSL-500-07-2 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 27 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 6 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 12A | 12C | X-500-17 | MCC | NIS | XSH-500-17-2 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 28 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 7 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 13A | 13C | X-500-34 | MCC | NIS | XSL-500-17-2 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 29 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 8 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 14A | 14C | X-500-34 | MCC | NIS | XSH-500-34-2 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 30 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 9 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 15A | 15C | X-500-44 | MCC | NIS | XSL-500-34-2 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 31 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 17 | 18 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 10 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 16A | 16C | X-500-44 | MCC | NIS | XSH-500-44-1 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 32 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 19 | 20 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 1A | 1C | X-500-194 | MCC | NIS | XSL-500-44-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 1 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-1 | DMC-001-006R | TB-C1-DO06R-1 | - | 21 | 22 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 2A | 2C | X-500-194 | MCC | NIS | XSH-500-194-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 2 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-1 | DMC-001-006R | TB-C1-DO06R-1 | - | 23 | 24 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 13 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 3A | 3C | X-500-204 | MCC | NIS | XSL-500-194-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 3 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-1 | DMC-001-006R | TB-C1-DO06R-1 | - | 25 | 26 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 14 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 4A | 4C | X-500-204 | MCC | NIS | XSH-500-204-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 4 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-1 | DMC-001-006R | TB-C1-DO06R-1 | - | 27 | 28 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 15 | NO | ACTIVE | MC-DM-IRP-500-007 | DOR | 5A | 5C | X-500-204 | MCC | NIS | XSL-500-204-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 5 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-1 | DMC-001-006R | TB-C1-DO06R-1 | - | 29 | 30 | - | DOR | DOR | NIS | MCC
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | Terminal Board (DO)-04 | Terminal Board | 16 | NO | HOT_SPARE | MC-DM-IRP-500-007 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 23 | TB2 | DSC-001-002R.C1-DO05R.TB2 /DMC-001-006R.TB-C1-DO05R-2 | DMC-001-006R | TB-C1-DO05R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 1A | 1B | X-110-41 | MCC | NIS | XA-110-41-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 17 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 2A | 2B | X-110-41 | MCC | NIS | XL-110-41-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 18 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 3A | 3B | X-110-41 | MCC | NIS | XLP-110-41-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 19 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 4A | 4B | X-110-41 | MCC | NIS | XXL-110-41-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 20 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 5A | 5B | X-110-44 | MCC | NIS | XA-110-44-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 21 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 6A | 6B | X-110-44 | MCC | NIS | XL-110-44-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 22 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 7A | 7B | X-110-44 | MCC | NIS | XLP-110-44-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 23 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 8A | 8B | X-110-44 | MCC | NIS | XXL-110-44-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 24 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 9A | 9B | X-110-47 | MCC | NIS | XA-110-47-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 25 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 10A | 10B | X-110-47 | MCC | NIS | XL-110-47-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 26 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 11A | 11B | X-110-47 | MCC | NIS | XLP-110-47-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 27 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-110-002 | DI | 12A | 12B | X-110-47 | MCC | NIS | XXL-110-47-2 | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 28 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 13 | YES | HOT_SPARE | MC-DM-IRP-110-002 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 17 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 14 | YES | HOT_SPARE | MC-DM-IRP-110-002 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 14 | C1-DI05 | L2-5 | DI05 | - | 17 | TB2 | DSC-001-002F.C1-DI05.TB2 /DMC-001-005F.TB-C1-DI05-2 | DMC-001-005F | TB-C1-DI05-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 11A | 11B | X-500-34 | MCC | NIS | XA-500-34-3 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 27 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-01 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 12A | 12B | X-500-34 | MCC | NIS | XL-500-34-3 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 28 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 13A | 13B | X-500-34 | MCC | NIS | XLP-500-34-3 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 29 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 14A | 14B | X-500-34 | MCC | NIS | XXL-500-34-3 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 30 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 15A | 15B | X-500-194 | MCC | NIS | XA-500-194-3 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 31 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 16A | 16B | X-500-194 | MCC | NIS | XL-500-194-3 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 32 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 1A | 1B | X-500-194 | MCC | NIS | XLP-500-194-3 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 1 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 2A | 2B | X-500-194 | MCC | NIS | XXL-500-194-3 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 2 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 3A | 3B | X-500-204 | MCC | NIS | XA-500-204-3 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 3 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 4A | 4B | X-500-204 | MCC | NIS | XL-500-204-3 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 4 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 5A | 5B | X-500-204 | MCC | NIS | XLP-500-204-3 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 5 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-500-001 | DI | 6A | 6B | X-500-204 | MCC | NIS | XXL-500-204-3 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 6 | TB1 | DSC-001-002F.C1-DI11.TB1 /DMC-001-006R.TB-C1-DI11-1 | DMC-001-006R | TB-C1-DI11-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 11 | YES | HOT_SPARE | MC-DM-IRP-500-001 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 27 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 12 | YES | HOT_SPARE | MC-DM-IRP-500-001 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI10 | L2-10 | DI10 | - | 27 | TB2 | DSC-001-002F.C1-DI10.TB2 /DMC-001-006R.TB-C1-DI10-2 | DMC-001-006R | TB-C1-DI10-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-500-003 | DI | 16A | 16B | X-500-194 | MCC | NIS | XA-500-194-1 | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 32 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-500-003 | DI | 1A | 1B | X-500-194 | MCC | NIS | XL-500-194-1 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 1 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-500-003 | DI | 2A | 2B | X-500-194 | MCC | NIS | XLP-500-194-1 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 2 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-02 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-500-003 | DI | 3A | 3B | X-500-194 | MCC | NIS | XXL-500-194-1 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 3 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-500-003 | DI | 4A | 4B | X-500-204 | MCC | NIS | XA-500-204-1 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 4 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-500-003 | DI | 5A | 5B | X-500-204 | MCC | NIS | XL-500-204-1 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 5 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-500-003 | DI | 6A | 6B | X-500-204 | MCC | NIS | XLP-500-204-1 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 6 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-500-003 | DI | 7A | 7B | X-500-204 | MCC | NIS | XXL-500-204-1 | FREE CONTACT | DCS | DSC-001-002F | 16 | C1-DI12 | L2-12 | DI12 | - | 7 | TB1 | DSC-001-002F.C1-DI12.TB1 /DMC-001-006R.TB-C1-DI12-1 | DMC-001-006R | TB-C1-DI12-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 5 | YES | HOT_SPARE | MC-DM-IRP-500-003 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 32 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 6 | YES | HOT_SPARE | MC-DM-IRP-500-003 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 13 | C1-DI11 | L2-11 | DI11 | - | 32 | TB2 | DSC-001-002F.C1-DI11.TB2 /DMC-001-006R.TB-C1-DI11-2 | DMC-001-006R | TB-C1-DI11-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 1A | 1B | X-500-44 | MCC | NIS | XA-500-44-1 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-12 | DI13 | - | 1 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 2A | 2B | X-500-44 | MCC | NIS | XL-500-44-1 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-12 | DI13 | - | 2 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 3A | 3B | X-500-44 | MCC | NIS | XLP-500-44-1 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-12 | DI13 | - | 3 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 4A | 4B | X-500-44 | MCC | NIS | XXL-500-44-1 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 4 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 5A | 5B | X-500-194 | MCC | NIS | XA-500-194-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 5 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 6A | 6B | X-500-194 | MCC | NIS | XL-500-194-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 6 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 7A | 7B | X-500-194 | MCC | NIS | XLP-500-194-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 7 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 8A | 8B | X-500-194 | MCC | NIS | XXL-500-194-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 8 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 9A | 9B | X-500-204 | MCC | NIS | XA-500-204-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 9 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-03 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 10A | 10B | X-500-204 | MCC | NIS | XL-500-204-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 10 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 11A | 11B | X-500-204 | MCC | NIS | XLP-500-204-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 11 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-500-005 | DI | 12A | 12B | X-500-204 | MCC | NIS | XXL-500-204-2 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 12 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 3 | YES | HOT_SPARE | MC-DM-IRP-500-005 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-12 | DI13 | - | 1 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 4 | YES | HOT_SPARE | MC-DM-IRP-500-005 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-12 | DI13 | - | 1 | TB1 | DSC-001-002F.C1-DI13.TB1 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-700-001 | DI | 1A | 1B | X-700-633 | MCC | NIS | XA-700-633 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 17 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-700-001 | DI | 2A | 2B | X-700-633 | MCC | NIS | XL-700-633 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 18 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-700-001 | DI | 3A | 3B | X-700-633 | MCC | NIS | XLP-700-633 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 19 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-700-001 | DI | 4A | 4B | X-700-633 | MCC | NIS | XXL-700-633 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 20 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-700-001 | DI | 5A | 5B | X-700-632 | MCC | NIS | XA-700-632 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 21 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-700-001 | DI | 6A | 6B | X-700-632 | MCC | NIS | XL-700-632 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 22 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-700-001 | DI | 7A | 7B | X-700-632 | MCC | NIS | XLP-700-632 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 23 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-700-001 | DI | 8A | 8B | X-700-632 | MCC | NIS | XXL-700-632 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 24 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 13 | YES | HOT_SPARE | MC-DM-IRP-700-001 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 17 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 14 | YES | HOT_SPARE | MC-DM-IRP-700-001 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 17 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-1 | DMC-001-005R | TB-C1-DI13-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 15 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 8A | 8B | P-3193-01 | MCC | NIS | XA-930-510 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 8 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-04 | Terminal Board | 16 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 9A | 9B | P-3193-01 | MCC | NIS | XL-930-510 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 9 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 10A | 10B | P-3193-01 | MCC | NIS | XLP-930-510 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 10 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 11A | 11B | P-3193-01 | MCC | NIS | XXL-930-510 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 11 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 12A | 12B | P-3193-02 | MCC | NIS | XA-930-511A | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 12 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 9 | 10 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 13A | 13B | P-3193-02 | MCC | NIS | XL-930-511A | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 13 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 11 | 12 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 14A | 14B | P-3193-02 | MCC | NIS | XLP-930-511A | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 14 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 13 | 14 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 15A | 15B | P-3193-02 | MCC | NIS | XXL-930-511A | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 15 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 15 | 16 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 16A | 16B | XA-930-508A | MCC | NIS | XA-930-508A | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 16 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 17 | 18 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 1A | 1B | XL-930-508A | MCC | NIS | XL-930-508A | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 17 | TB2 | DSC-001-002F.C1-DI14.TB2 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 19 | 20 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 2A | 2B | XLP-930-508A | MCC | NIS | XLP-930-508A | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 18 | TB2 | DSC-001-002F.C1-DI14.TB2 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 21 | 22 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 10 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 3A | 3B | XXL-930-508A | MCC | NIS | XXL-930-508A | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 19 | TB2 | DSC-001-002F.C1-DI14.TB2 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 23 | 24 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 11 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 4A | 4B | XA-930-509 | MCC | NIS | XA-930-509 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 20 | TB2 | DSC-001-002F.C1-DI14.TB2 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 25 | 26 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 12 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 5A | 5B | XL-930-509 | MCC | NIS | XL-930-509 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 21 | TB2 | DSC-001-002F.C1-DI14.TB2 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 27 | 28 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 13 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 6A | 6B | XLP-930-509 | MCC | NIS | XLP-930-509 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 22 | TB2 | DSC-001-002F.C1-DI14.TB2 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 29 | 30 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 14 | YES | ACTIVE | MC-DM-IRP-930-002 | DI | 7A | 7B | XXL-930-509 | MCC | NIS | XXL-930-509 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 23 | TB2 | DSC-001-002F.C1-DI14.TB2 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 31 | 32 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 15 | YES | HOT_SPARE | MC-DM-IRP-930-002 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 8 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DI)-05 | Terminal Board | 16 | YES | ACTIVE | I-120-561-2 | DIR | 6A | 6B | X-120-561 | UCP | NIS | I-120-561-2 | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 6 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 | - | DIR | DIR | NIS | UCP
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 1 | NO | ACTIVE | JB-DND-450-001 | DOR | 13A | 13C | L-450-16 | FIELD | NIS | LA-450-16 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 29 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 2 | NO | ACTIVE | JB-DND-450-001 | DOR | 14A | 14C | L-450-22 | FIELD | NIS | LA-450-22 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 30 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 3 | 4 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 3 | NO | HOT_SPARE | JB-DND-450-001 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 29 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 4 | NO | HOT_SPARE | JB-DND-450-001 | DOR | T3 | T4 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 29 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 5 | NO | ACTIVE | JB-DNS-110-001 | DOR | 11A | 11C | U-900-02 | FIELD | NIS | UY-900-02 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 11 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 6 | NO | ACTIVE | JB-DNS-110-001 | DOR | 12A | 12C | U-900-03 | FIELD | NIS | UY-900-03 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 12 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 3 | 4 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 7 | NO | HOT_SPARE | JB-DNS-110-001 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 11 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 8 | NO | HOT_SPARE | JB-DNS-110-001 | DOR | T3 | T4 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 11 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 9 | NO | ACTIVE | JB-DNS-450-001 | DOR | 2A | 2C | U-450-01 | FIELD | NIS | UY-450-01 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 18 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 10 | NO | ACTIVE | JB-DNS-450-001 | DOR | 3A | 3C | U-450-02 | FIELD | NIS | UY-450-02 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 19 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 3 | 4 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 11 | NO | ACTIVE | JB-DNS-450-001 | DOR | 4A | 4C | U-450-03 | FIELD | NIS | UY-450-03 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 20 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 5 | 6 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 12 | NO | ACTIVE | JB-DNS-450-001 | DOR | 5A | 5C | U-450-04 | FIELD | NIS | UY-450-04 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 21 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 7 | 8 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 13 | NO | HOT_SPARE | JB-DNS-450-001 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 18 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 14 | NO | HOT_SPARE | JB-DNS-450-001 | DOR | T3 | T4 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 18 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 15 | NO | ACTIVE | SV-930-532 | DOR | 16A | 16C | - | FIELD | NIS | SV-930-532 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 32 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | Terminal Board (DO)-01 | Terminal Board | 16 | NO | HOT_SPARE | SV-930-532 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 32 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 1 | NO | ACTIVE | HOLD-C-3111-01ABS | DIR | 11A | 11B | C-3111-01A | UCP | NIS | XS-110-503A | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 11 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 7 | 8 | - | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 2 | NO | ACTIVE | HOLD-C-3111-01ABS | DIR | 12A | 12B | C-3111-01B | UCP | NIS | XS-110-503B | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 12 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 9 | 10 | - | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 3 | NO | ACTIVE | HOLD-C-3111-01ABS | DIR | 13A | 13B | C-3111-01S | UCP | NIS | XS-110-503S | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 13 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 11 | 12 | - | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 4 | NO | HOT_SPARE | HOLD-C-3111-01ABS | DIR | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 11 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 7 | 8 | - | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 5 | NO | ACTIVE | I-120-571-1 | DIR | 7A | 7B | X-120-571 | UCP | NIS | I-120-571-1 | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 7 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 | - | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 6 | NO | ACTIVE | I-120-571-2 | DIR | 8A | 8B | X-120-571 | UCP | NIS | I-120-571-2 | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 | - | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 7 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 8 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 9 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 10 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 11 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 12 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 13 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 14 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 15 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 16 | NO | SPARE | I-120-571-2 | DIR |  |  | SPARE | UCP | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 8 | TB1 | DSC-001-002F.C1-DI01R.TB1 /DMC-001-004R.TB-C1-DI01R-1 | DMC-001-004R | TB-C1-DI01R-1 | - | 1 | 2 |  | DIR | DIR | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 1 | NO | ACTIVE | HOLD-C-3111-01ABS | DO | 7A | 7C | C-3111-01A | UCP | NIS | XS-110-502A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 23 | TB2 | DSC-001-002R.C1-DO07.TB2 /DMC-001-004R.TB-C1-DO07-2 | DMC-001-004R | TB-C1-DO07-2 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 2 | NO | ACTIVE | HOLD-C-3111-01ABS | DO | 8A | 8C | C-3111-01B | UCP | NIS | XS-110-502B | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 24 | TB2 | DSC-001-002R.C1-DO07.TB2 /DMC-001-004R.TB-C1-DO07-2 | DMC-001-004R | TB-C1-DO07-2 | - | 3 | 4 | - | DO | DO | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 3 | NO | ACTIVE | HOLD-C-3111-01ABS | DO | 9A | 9C | C-3111-01S | UCP | NIS | XS-110-502S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 25 | TB2 | DSC-001-002R.C1-DO07.TB2 /DMC-001-004R.TB-C1-DO07-2 | DMC-001-004R | TB-C1-DO07-2 | - | 5 | 6 | - | DO | DO | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 4 | NO | HOT_SPARE | HOLD-C-3111-01ABS | DO | T3 | T4 | HOT_SPARE | UCP | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 23 | TB2 | DSC-001-002R.C1-DO07.TB2 /DMC-001-004R.TB-C1-DO07-2 | DMC-001-004R | TB-C1-DO07-2 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 5 | NO | ACTIVE | XS-110-505S | DO | 3A | 3C | X-110-505S | UCP | NIS | XS-110-505S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 3 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 6 | NO | ACTIVE | JB-DNS-450-002 | DOR | 9A | 9C | U-450-111 | FIELD | NIS | UY-450-111 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 25 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 7 | NO | ACTIVE | JB-DNS-450-002 | DOR | 10A | 10C | U-450-112 | FIELD | NIS | UY-450-112 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 26 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 3 | 4 | - | DOR | DOR | NIS | FIELD
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 8 | NO | HOT_SPARE | JB-DNS-450-002 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 25 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 9 | NO | HOT_SPARE | JB-DNS-450-002 | DOR | T3 | T4 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 25 | TB2 | DSC-001-002R.C1-DO01R.TB2 /DMC-001-004R.TB-C1-DO01R-2 | DMC-001-004R | TB-C1-DO01R-2 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 10 | NO | ACTIVE | MC-DM-IRP-110-003 | DOR | 1A | 1C | X-110-41 | MCC | NIS | XSH-110-41-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 1 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-110-003 | DOR | 2A | 2C | X-110-41 | MCC | NIS | XSL-110-41-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 2 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-110-003 | DOR | 3A | 3C | X-110-44 | MCC | NIS | XSH-110-44-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 3 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 13 | NO | ACTIVE | MC-DM-IRP-110-003 | DOR | 4A | 4C | X-110-44 | MCC | NIS | XSL-110-44-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 4 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 14 | NO | ACTIVE | MC-DM-IRP-110-003 | DOR | 5A | 5C | X-110-47 | MCC | NIS | XSH-110-47-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 5 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 15 | NO | ACTIVE | MC-DM-IRP-110-003 | DOR | 6A | 6C | X-110-47 | MCC | NIS | XSL-110-47-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 6 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 16 | NO | HOT_SPARE | MC-DM-IRP-110-003 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 1 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 1 | NO | ACTIVE | MC-DM-IRP-110-004 | DOR | 8A | 8C | X-110-41 | MCC | NIS | XSH-110-41-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 8 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 2 | NO | ACTIVE | MC-DM-IRP-110-004 | DOR | 9A | 9C | X-110-41 | MCC | NIS | XSL-110-41-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 9 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 3 | NO | ACTIVE | MC-DM-IRP-110-004 | DOR | 10A | 10C | X-110-44 | MCC | NIS | XSH-110-44-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 10 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 4 | NO | ACTIVE | MC-DM-IRP-110-004 | DOR | 11A | 11C | X-110-44 | MCC | NIS | XSL-110-44-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 11 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 5 | NO | ACTIVE | MC-DM-IRP-110-004 | DOR | 12A | 12C | X-110-47 | MCC | NIS | XSH-110-47-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 12 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 6 | NO | ACTIVE | MC-DM-IRP-110-004 | DOR | 13A | 13C | X-110-47 | MCC | NIS | XSL-110-47-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 13 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 7 | NO | HOT_SPARE | MC-DM-IRP-110-004 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 8 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 8 | NO | ACTIVE | MC-DM-IRP-120-003 | DOR | 15A | 15C | X-120-61 | MCC | NIS | XSH-120-61-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 15 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 9 | NO | ACTIVE | MC-DM-IRP-120-003 | DOR | 16A | 16C | X-120-61 | MCC | NIS | XSL-120-61-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 16 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 10 | NO | ACTIVE | MC-DM-IRP-120-003 | DOR | 1A | 1C | X-120-31 | MCC | NIS | XSH-120-31-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 17 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-120-003 | DOR | 2A | 2C | X-120-31 | MCC | NIS | XSL-120-31-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 18 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-120-003 | DOR | 3A | 3C | X-120-50 | MCC | NIS | XSH-120-50-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 19 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 13 | NO | ACTIVE | MC-DM-IRP-120-003 | DOR | 4A | 4C | X-120-50 | MCC | NIS | XSL-120-50-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 20 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 14 | NO | ACTIVE | MC-DM-IRP-120-003 | DOR | 5A | 5C | X-120-52 | MCC | NIS | XSH-120-52-A | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 21 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 15 | NO | ACTIVE | MC-DM-IRP-120-003 | DOR | 6A | 6C | X-120-52 | MCC | NIS | XSL-120-52-A | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 22 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 16 | NO | HOT_SPARE | MC-DM-IRP-120-003 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 15 | TB1 | DSC-001-002R.C1-DO02R.TB1 /DMC-001-005R.TB-C1-DO02R-1 | DMC-001-005R | TB-C1-DO02R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 1 | NO | ACTIVE | MC-DM-IRP-120-004 | DOR | 11A | 11C | X-120-61 | MCC | NIS | XSH-120-61-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 27 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 2 | NO | ACTIVE | MC-DM-IRP-120-004 | DOR | 12A | 12C | X-120-61 | MCC | NIS | XSL-120-61-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 28 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 3 | NO | ACTIVE | MC-DM-IRP-120-004 | DOR | 13A | 13C | X-120-31 | MCC | NIS | XSH-120-31-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 29 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 4 | NO | ACTIVE | MC-DM-IRP-120-004 | DOR | 14A | 14C | X-120-31 | MCC | NIS | XSL-120-31-2 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 30 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 5 | NO | ACTIVE | MC-DM-IRP-120-004 | DOR | 15A | 15C | X-120-50 | MCC | NIS | XSH-120-50-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 31 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 6 | NO | ACTIVE | MC-DM-IRP-120-004 | DOR | 16A | 16C | X-120-50 | MCC | NIS | XSL-120-50-1 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 32 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 7 | NO | ACTIVE | MC-DM-IRP-120-004 | DOR | 1A | 1C | X-120-52 | MCC | NIS | XSH-120-52-S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 1 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 8 | NO | ACTIVE | MC-DM-IRP-120-004 | DOR | 2A | 2C | X-120-52 | MCC | NIS | XSL-120-52-S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 2 | TB1 | DSC-001-002R.C1-DO03R.TB1 /DMC-001-005R.TB-C1-DO03R-1 | DMC-001-005R | TB-C1-DO03R-1 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 9 | NO | HOT_SPARE | MC-DM-IRP-120-004 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO02R | L2-19 | DO02 | DO02R | 27 | TB2 | DSC-001-002R.C1-DO02R.TB2 /DMC-001-005R.TB-C1-DO02R-2 | DMC-001-005R | TB-C1-DO02R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 10 | NO | ACTIVE | MC-DM-IRP-120-009 | DOR | 3A | 3C | X-120-88 | MCC | NIS | XSH-120-88S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 19 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-120-009 | DOR | 4A | 4C | X-120-88 | MCC | NIS | XSL-120-88S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 20 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-120-009 | DOR | 5A | 5C | X-120-623S | MCC | NIS | XSH-120-623S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 21 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 13 | NO | ACTIVE | MC-DM-IRP-120-009 | DOR | 6A | 6C | X-120-623S | MCC | NIS | XSL-120-623S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 22 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 14 | NO | ACTIVE | MC-DM-IRP-120-009 | DOR | 7A | 7C | X-120-622S | MCC | NIS | XSH-120-622S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 23 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 15 | NO | ACTIVE | MC-DM-IRP-120-009 | DOR | 8A | 8C | X-120-622S | MCC | NIS | XSL-120-622S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 24 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 16 | NO | ACTIVE | MC-DM-IRP-120-009 | DOR | 9A | 9C | X-120-98 | MCC | NIS | XSH-120-98A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 25 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 1 | NO | ACTIVE | MC-DM-IRP-120-009 | DOR | 10A | 10C | X-120-98 | MCC | NIS | XSL-120-98A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 26 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 2 | NO | HOT_SPARE | MC-DM-IRP-120-009 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 19 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 3 | NO | ACTIVE | MC-DM-IRP-700-002 | DOR | 11A | 11C | X-700-633 | MCC | NIS | XSH-700-633 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 11 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-1 | DMC-001-006R | TB-C1-DO06R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 4 | NO | ACTIVE | MC-DM-IRP-700-002 | DOR | 12A | 12C | X-700-633 | MCC | NIS | XSL-700-633 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 12 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-1 | DMC-001-006R | TB-C1-DO06R-1 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 5 | NO | ACTIVE | MC-DM-IRP-700-002 | DOR | 13A | 13C | X-700-632 | MCC | NIS | XSH-700-632 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 13 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-1 | DMC-001-006R | TB-C1-DO06R-1 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 6 | NO | ACTIVE | MC-DM-IRP-700-002 | DOR | 14A | 14C | X-700-632 | MCC | NIS | XSL-700-632 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 14 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 7 | NO | HOT_SPARE | MC-DM-IRP-700-002 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 11 | TB1 | DSC-001-002R.C1-DO06R.TB1 /DMC-001-006R.TB-C1-DO06R-1 | DMC-001-006R | TB-C1-DO06R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 8 | NO | ACTIVE | MC-DM-IRP-930-004 | DOR | 6A | 6C | P-3193-01 | MCC | NIS | XSH-930-510 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 22 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 9 | NO | ACTIVE | MC-DM-IRP-930-004 | DOR | 7A | 7C | P-3193-01 | MCC | NIS | XSL-930-510 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 23 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 10 | NO | ACTIVE | MC-DM-IRP-930-004 | DOR | 8A | 8C | P-3193-02 | MCC | NIS | XSH-930-511A | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 24 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 5 | 6 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-930-004 | DOR | 9A | 9C | P-3193-02 | MCC | NIS | XSL-930-511A | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 25 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 7 | 8 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-930-004 | DOR | 10A | 10C | P-3193-05A | MCC | NIS | XSH-930-508A | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 26 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 9 | 10 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 13 | NO | ACTIVE | MC-DM-IRP-930-004 | DOR | 11A | 11C | P-3193-05A | MCC | NIS | XSL-930-508A | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 27 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 11 | 12 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 14 | NO | ACTIVE | MC-DM-IRP-930-004 | DOR | 12A | 12C | P-3193-06 | MCC | NIS | XSH-930-509 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 28 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 13 | 14 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 15 | NO | ACTIVE | MC-DM-IRP-930-004 | DOR | 13A | 13C | P-3193-06 | MCC | NIS | XSL-930-509 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 29 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 15 | 16 | - | DOR | DOR | NIS | MCC
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-04 | Terminal Board | 16 | NO | HOT_SPARE | MC-DM-IRP-930-004 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 22 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-700-009 | DI | 12A | 12B | X-700-88 | MCC | NIS | XA-700-88 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 28 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 2 | YES | ACTIVE | MC-DM-IRP-700-009 | DI | 13A | 13B | X-700-88 | MCC | NIS | XL-700-88 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 29 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 3 | YES | ACTIVE | MC-DM-IRP-700-009 | DI | 14A | 14B | X-700-88 | MCC | NIS | XLP-700-88 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 30 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-700-009 | DI | 15A | 15B | X-700-88 | MCC | NIS | XXL-700-88 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 31 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 5 | YES | HOT_SPARE | MC-DM-IRP-700-009 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 28 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 6 | YES | HOT_SPARE | MC-DM-IRP-700-009 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 28 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-900-001 | DI | 16A | 16B | X-900-01 | MCC | NIS | XA-900-01 | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 32 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 8 | YES | ACTIVE | MC-DM-IRP-900-001 | DI | 1A | 1B | X-900-01 | MCC | NIS | XL-900-01 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 1 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 9 | YES | ACTIVE | MC-DM-IRP-900-001 | DI | 2A | 2B | X-900-01 | MCC | NIS | XLP-900-01 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 2 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 10 | NO | SPARE | MC-DM-IRP-900-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 2 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 5 | 6 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 11 | NO | SPARE | MC-DM-IRP-900-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 2 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 5 | 6 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 12 | NO | SPARE | MC-DM-IRP-900-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 2 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 5 | 6 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 13 | NO | SPARE | MC-DM-IRP-900-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 2 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 5 | 6 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 14 | NO | SPARE | MC-DM-IRP-900-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 2 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 5 | 6 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 15 | NO | SPARE | MC-DM-IRP-900-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 2 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 5 | 6 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-01 | Terminal Board | 16 | NO | SPARE | MC-DM-IRP-900-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 2 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 5 | 6 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-900-001 | DI | 3A | 3B | X-900-01 | MCC | NIS | XXL-900-01 | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 3 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-2 | DMC-001-005R | TB-C1-DI14-2 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 2 | YES | HOT_SPARE | MC-DM-IRP-900-001 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 32 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 3 | YES | HOT_SPARE | MC-DM-IRP-900-001 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 7 | C1-DI13 | L2-13 | DI13 | - | 32 | TB2 | DSC-001-002F.C1-DI13.TB2 /DMC-001-005R.TB-C1-DI13-2 | DMC-001-005R | TB-C1-DI13-2 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 4 | YES | ACTIVE | MC-DM-IRP-930-001 | DI | 4A | 4B | P-3193-05B | MCC | NIS | XA-930-508S | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 5 | YES | ACTIVE | MC-DM-IRP-930-001 | DI | 5A | 5B | P-3193-05B | MCC | NIS | XL-930-508S | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 5 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 3 | 4 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 6 | YES | ACTIVE | MC-DM-IRP-930-001 | DI | 6A | 6B | P-3193-05B | MCC | NIS | XLP-930-508S | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 6 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 5 | 6 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 7 | YES | ACTIVE | MC-DM-IRP-930-001 | DI | 7A | 7B | P-3193-05B | MCC | NIS | XXL-930-508S | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 7 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 7 | 8 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 8 | YES | HOT_SPARE | MC-DM-IRP-930-001 | DI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 9 | YES | HOT_SPARE | MC-DM-IRP-930-001 | DI | T3 | T4 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 | - | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 10 | NO | SPARE | MC-DM-IRP-930-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 11 | NO | SPARE | MC-DM-IRP-930-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 12 | NO | SPARE | MC-DM-IRP-930-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 13 | NO | SPARE | MC-DM-IRP-930-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 14 | NO | SPARE | MC-DM-IRP-930-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 15 | NO | SPARE | MC-DM-IRP-930-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DI)-02 | Terminal Board | 16 | NO | SPARE | MC-DM-IRP-930-001 | DI |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002F | 10 | C1-DI14 | L2-14 | DI14 | - | 4 | TB1 | DSC-001-002F.C1-DI14.TB1 /DMC-001-005R.TB-C1-DI14-1 | DMC-001-005R | TB-C1-DI14-1 | - | 1 | 2 |  | DI | DI | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 1 | NO | ACTIVE | XS-000-501 | DO | 1A | 1C | - | UCP | NIS | XS-000-501 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 17 | TB2 | DSC-001-002R.C1-DO07.TB2 /DMC-001-004R.TB-C1-DO07-2 | DMC-001-004R | TB-C1-DO07-2 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 2 | NO | HOT_SPARE | XS-000-501 | DO | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 17 | TB2 | DSC-001-002R.C1-DO07.TB2 /DMC-001-004R.TB-C1-DO07-2 | DMC-001-004R | TB-C1-DO07-2 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 3 | NO | ACTIVE | XS-000-601 | DO | 2A | 2C | - | UCP | NIS | XS-000-601 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 18 | TB2 | DSC-001-002R.C1-DO07.TB2 /DMC-001-004R.TB-C1-DO07-2 | DMC-001-004R | TB-C1-DO07-2 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 4 | NO | HOT_SPARE | XS-000-601 | DO | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 18 | TB2 | DSC-001-002R.C1-DO07.TB2 /DMC-001-004R.TB-C1-DO07-2 | DMC-001-004R | TB-C1-DO07-2 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 5 | NO | ACTIVE | XS-110-505A | DO | 1A | 1C | X-110-505A | UCP | NIS | XS-110-505A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 1 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 6 | NO | HOT_SPARE | XS-110-505A | DO | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 1 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 7 | NO | ACTIVE | XS-110-505B | DO | 2A | 2C | X-110-505B | UCP | NIS | XS-110-505B | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 2 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 8 | NO | HOT_SPARE | XS-110-505B | DO | T1 | T2 | HOT_SPARE | UCP | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 2 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 9 | NO | ACTIVE | XS-120-532 | DO | 4A | 4C | X-120-532 | UCP | NIS | XS-120-532 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 4 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 10 | NO | ACTIVE | XS-120-541 | DO | 5A | 5C | X-120-541 | UCP | NIS | XS-120-541 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 5 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 11 | NO | ACTIVE | XS-120-562 | DO | 6A | 6C | X-120-562 | UCP | NIS | XS-120-562 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 6 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 12 | NO | ACTIVE | XS-120-571 | DO | 7A | 7C | X-120-571 | UCP | NIS | XS-120-571 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 7 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 13 | NO | ACTIVE | XS-450-532 | DO | 8A | 8C | X-450-532 | UCP | NIS | XS-450-532 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 8 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 14 | NO | SPARE | XS-450-532 | DO |  |  | SPARE | UCP | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 8 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 |  | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 15 | NO | SPARE | XS-450-532 | DO |  |  | SPARE | UCP | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 8 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 |  | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-01 | Terminal Board | 16 | NO | SPARE | XS-450-532 | DO |  |  | SPARE | UCP | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 8 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 |  | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 1 | NO | ACTIVE | XS-450-552 | DO | 9A | 9C | X-450-552 | UCP | NIS | XS-450-552 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 9 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 2 | NO | ACTIVE | XS-450-572 | DO | 10A | 10C | X-450-572 | UCP | NIS | XS-450-572 | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 10 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 3 | NO | ACTIVE | XS-500-501A | DO | 11A | 11C | - | UCP | NIS | XS-500-501A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 11 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 4 | NO | ACTIVE | XS-500-501S | DO | 12A | 12C | - | UCP | NIS | XS-500-501S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 12 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 5 | NO | ACTIVE | XS-500-502A | DO | 13A | 13C | - | UCP | NIS | XS-500-502A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 13 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 6 | NO | ACTIVE | XS-500-502S | DO | 14A | 14C | - | UCP | NIS | XS-500-502S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 14 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 7 | NO | ACTIVE | XS-500-505A | DO | 15A | 15C | - | UCP | NIS | XS-500-505A | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 15 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 8 | NO | ACTIVE | XS-500-505S | DO | 16A | 16C | - | UCP | NIS | XS-500-505S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO07 | L2-24 | DO07 | - | 16 | TB1 | DSC-001-002R.C1-DO07.TB1 /DMC-001-004R.TB-C1-DO07-1 | DMC-001-004R | TB-C1-DO07-1 | - | 1 | 2 | - | DO | DO | NIS | UCP
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 9 | NO | ACTIVE | UY-002-001 | DOR | 3A | 3C | UV-002-001 | FIELD | NIS | UY-002-001 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 3 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 10 | NO | HOT_SPARE | UY-002-001 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 3 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 11 | NO | ACTIVE | UY-200-07 | DOR | 2A | 2C | U-200-07 | FIELD | NIS | UY-200-07 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 2 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 12 | NO | HOT_SPARE | UY-200-07 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 2 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 13 | NO | ACTIVE | UY-700-81 | DOR | 1A | 1C | U-700-81 | FIELD | NIS | UY-700-81 | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 1 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 14 | NO | SPARE | UY-700-81 | DOR |  |  | SPARE | FIELD | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 1 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 |  | DOR | DOR | NIS | FIELD
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 15 | NO | SPARE | UY-700-81 | DOR |  |  | SPARE | FIELD | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 1 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 |  | DOR | DOR | NIS | FIELD
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-02 | Terminal Board | 16 | NO | SPARE | UY-700-81 | DOR |  |  | SPARE | FIELD | NIS | SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 1 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 |  | DOR | DOR | NIS | FIELD
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 1 | NO | HOT_SPARE | UY-700-81 | DOR | T1 | T2 | HOT_SPARE | FIELD | NIS | HOT_SPARE | 24 VDC-P | DCS | DSC-001-002R | 1 | C1-DO01R | L2-18 | DO01 | DO01R | 1 | TB1 | DSC-001-002R.C1-DO01R.TB1 /DMC-001-004R.TB-C1-DO01R-1 | DMC-001-004R | TB-C1-DO01R-1 | - | 1 | 2 | - | DOR | DOR | NIS | FIELD
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 2 | NO | ACTIVE | MC-DM-IRP-450-008 | DOR | 1A | 1C | X-450-22 | MCC | NIS | XSH-450-22 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 1 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 3 | NO | ACTIVE | MC-DM-IRP-450-008 | DOR | 2A | 2C | X-450-22 | MCC | NIS | XSL-450-22 | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 2 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 4 | NO | HOT_SPARE | MC-DM-IRP-450-008 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 1 | C1-DO05R | L2-22 | DO05 | DO05R | 1 | TB1 | DSC-001-002R.C1-DO05R.TB1 /DMC-001-006R.TB-C1-DO05R-1 | DMC-001-006R | TB-C1-DO05R-1 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 5 | NO | ACTIVE | MC-DM-IRP-700-010 | DOR | 15A | 15C | X-700-88 | MCC | NIS | XSH-700-88 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 31 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 6 | NO | ACTIVE | MC-DM-IRP-700-010 | DOR | 16A | 16C | X-700-88 | MCC | NIS | XSL-700-88 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 32 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 7 | NO | HOT_SPARE | MC-DM-IRP-700-010 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 31 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 8 | NO | ACTIVE | MC-DM-IRP-900-002 | DOR | 3A | 3C | X-900-01 | MCC | NIS | XSH-900-01 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 19 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 9 | NO | ACTIVE | MC-DM-IRP-900-002 | DOR | 4A | 4C | X-900-01 | MCC | NIS | XSL-900-01 | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 20 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 10 | NO | HOT_SPARE | MC-DM-IRP-900-002 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 5 | C1-DO06R | L2-23 | DO06 | DO06R | 19 | TB2 | DSC-001-002R.C1-DO06R.TB2 /DMC-001-006R.TB-C1-DO06R-2 | DMC-001-006R | TB-C1-DO06R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 11 | NO | ACTIVE | MC-DM-IRP-930-003 | DOR | 13A | 13C | P-3193-05B | MCC | NIS | XSH-930-508S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 29 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 12 | NO | ACTIVE | MC-DM-IRP-930-003 | DOR | 14A | 14C | P-3193-05B | MCC | NIS | XSL-930-508S | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 30 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 3 | 4 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 13 | NO | HOT_SPARE | MC-DM-IRP-930-003 | DOR | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 29 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 1 | 2 | - | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 14 | NO | SPARE | MC-DM-IRP-930-003 | DOR |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 29 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 1 | 2 |  | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 15 | NO | SPARE | MC-DM-IRP-930-003 | DOR |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 29 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 1 | 2 |  | DOR | DOR | NIS | MCC
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | Terminal Board (DO)-03 | Terminal Board | 16 | NO | SPARE | MC-DM-IRP-930-003 | DOR |  |  | SPARE | MCC | NIS | SPARE | FREE CONTACT | DCS | DSC-001-002R | 9 | C1-DO03R | L2-20 | DO03 | DO03R | 29 | TB2 | DSC-001-002R.C1-DO03R.TB2 /DMC-001-005R.TB-C1-DO03R-2 | DMC-001-005R | TB-C1-DO03R-2 | - | 1 | 2 |  | DOR | DOR | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 1 | YES | ACTIVE | MC-DM-IRP-700-011 | AI | 1A | 1B | 0 | MCC | NIS | II-700-88 | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 | SC | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 2 | YES | HOT_SPARE | MC-DM-IRP-700-011 | AI | T1 | T2 | HOT_SPARE | MCC | NIS | HOT_SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 | SC | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 3 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 4 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 5 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 6 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 7 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 8 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 9 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 10 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 11 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 12 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 13 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 14 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 15 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | Terminal Board (AI)-01 | Terminal Board | 16 | NO | SPARE | MC-DM-IRP-700-011 | AI |  |  | SPARE | MCC | NIS | SPARE | 4-20 MA HART | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1 | 2 |  | AI | AI | NIS | MCC

## input_report
Cleaning Summary
Total_Raw | 797
Total_Clean | 792
Removed | 5
Removed / Critical (Missing Data)
(None)
Removed Invalid JBs
Loop No | Tag No | I/O Type | Voltage | IS/NIS | Location | To | Marshaling | idk | card | idk2 | card1 | card2 | channel | TB | all | system | real card | card-terminal | terminal-1 | terminal-2 | JB | terminal-1.1 | terminal-2.1 | SRC
DMC1-04-FAF | - | DI | 24 VDC-P | NIS | - | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 6 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 6A | 6B | - | - | - | -
DMC1-04-PWF | - | DI | 24 VDC-P | NIS | - | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 7 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 7A | 7B | - | - | - | -
DMC1-04-ERF | - | DI | 24 VDC-P | NIS | - | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 8 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 8A | 8B | - | - | - | -
DMC1-04-THF | - | DI | 24 VDC-P | NIS | - | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 9 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 9A | 9B | - | - | - | -
DMC1-04-DRF | - | DI | 24 VDC-P | NIS | - | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 10 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 10A | 10B | - | - | - | -
Invalid IO Types
(None)
Safety Conversions (Warning)
(None)
Location Imputed
Loop No | Tag No | I/O Type | Voltage | IS/NIS | Location | To | Marshaling | idk | card | idk2 | card1 | card2 | channel | TB | all | system | real card | card-terminal | terminal-1 | terminal-2 | JB | terminal-1.1 | terminal-2.1 | SRC | IO_RAW | IO_KEY | SAFETY_RAW | LOC_RAW
GPC1-03-FAF | - | DIR | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 29 | TB2 | DSC-001-002F.C1-DI01R.TB2 /DMC-001-004R.TB-C1-DI01R-2 | DMC-001-004R | TB-C1-DI01R-2 | - | 13A | 13B | IF-PDP-003 | 1 | 2 | - | DIR | DIR | NIS | -
GPC1-03-THF | - | DIR | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 30 | TB2 | DSC-001-002F.C1-DI01R.TB2 /DMC-001-004R.TB-C1-DI01R-2 | DMC-001-004R | TB-C1-DI01R-2 | - | 14A | 14B | IF-PDP-003 | 3 | 4 | - | DIR | DIR | NIS | -
GPC1-03-DRF | - | DIR | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 31 | TB2 | DSC-001-002F.C1-DI01R.TB2 /DMC-001-004R.TB-C1-DI01R-2 | DMC-001-004R | TB-C1-DI01R-2 | - | 15A | 15B | IF-PDP-003 | 5 | 6 | - | DIR | DIR | NIS | -
GPC1-03-ERF | - | DIR | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 1 | C1-DI01R | L2-1 | DI01 | DI01R | 32 | TB2 | DSC-001-002F.C1-DI01R.TB2 /DMC-001-004R.TB-C1-DI01R-2 | DMC-001-004R | TB-C1-DI01R-2 | - | 16A | 16B | IF-PDP-003 | 7 | 8 | - | DIR | DIR | NIS | -
DMC1-01-FAF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 1 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 |  | 1A | 1B | INTERNAL FAULT | 1 | 2 | - | DI | DI | NIS | -
DMC1-01-PWF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 2 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 2A | 2B | INTERNAL FAULT | 3 | 4 | - | DI | DI | NIS | -
DMC1-01-ERF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 3 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 3A | 3B | INTERNAL FAULT | 5 | 6 | - | DI | DI | NIS | -
DMC1-01-THF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 4 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 4A | 4B | INTERNAL FAULT | 7 | 8 | - | DI | DI | NIS | -
DMC1-01-DRF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 5 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 5A | 5B | INTERNAL FAULT | 9 | 10 | - | DI | DI | NIS | -
DMC1-05-FAF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 11 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 11A | 11B | INTERNAL FAULT | 11 | 12 | - | DI | DI | NIS | -
DMC1-05-THF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 12 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 12A | 12B | INTERNAL FAULT | 13 | 14 | - | DI | DI | NIS | -
DMC1-05-DRF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 13 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 13A | 13B | INTERNAL FAULT | 15 | 16 | - | DI | DI | NIS | -
DSC1-01-FAF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 14 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 14A | 14B | INTERNAL FAULT | 17 | 18 | - | DI | DI | NIS | -
DSC1-01-PWF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 15 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 15A | 15B | INTERNAL FAULT | 19 | 20 | - | DI | DI | NIS | -
DSC1-01-ERF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 16 | TB1 | DSC-001-002F.C1-DI16.TB1 /DMC-001-004R.TB-C1-DI16-1 | DMC-001-004R | TB-C1-DI16-1 | - | 16A | 16B | INTERNAL FAULT | 21 | 22 | - | DI | DI | NIS | -
DSC1-01-THF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 17 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 1A | 1B | INTERNAL FAULT | 23 | 24 | - | DI | DI | NIS | -
DSC1-01-DRF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 18 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 2A | 2B | INTERNAL FAULT | 25 | 26 | - | DI | DI | NIS | -
GNC1-01-FAF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 19 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 3A | 3B | INTERNAL FAULT | 27 | 28 | - | DI | DI | NIS | -
GNC1-01-PWF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 20 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 4A | 4B | INTERNAL FAULT | 29 | 30 | - | DI | DI | NIS | -
GNC1-01-THF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 21 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 5A | 5B | INTERNAL FAULT | 31 | 32 | - | DI | DI | NIS | -
GNC1-01-DRF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 22 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 6A | 6B | INTERNAL FAULT | 33 | 34 | - | DI | DI | NIS | -
GPC1-01-FAF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 23 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 | - | 7A | 7B | INTERNAL FAULT | 35 | 36 | - | DI | DI | NIS | -
GPC1-01-THF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 24 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 8A | 8B | INTERNAL FAULT | 37 | 38 | - | DI | DI | NIS | -
GPC1-01-DRF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 25 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 9A | 9B | INTERNAL FAULT | 39 | 40 | - | DI | DI | NIS | -
GPC1-01-ERF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 26 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 10A | 10B | INTERNAL FAULT | 41 | 42 | - | DI | DI | NIS | -
GPC1-02-FAF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 27 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 11A | 11B | INTERNAL FAULT | 43 | 44 | - | DI | DI | NIS | -
GPC1-02-THF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 28 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 12A | 12B | INTERNAL FAULT | 45 | 46 | - | DI | DI | NIS | -
GPC1-02-DRF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 29 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 13A | 13B | INTERNAL FAULT | 47 | 48 | - | DI | DI | NIS | -
GPC1-02-ERF | - | DI | 24 VDC-P | NIS | nan | DCS | DSC-001-002F | 16 | C1-DI16 | L2-16 | DI16 | - | 30 | TB2 | DSC-001-002F.C1-DI16.TB2 /DMC-001-004R.TB-C1-DI16-2 | DMC-001-004R | TB-C1-DI16-2 |  | 14A | 14B | INTERNAL FAULT | 49 | 50 | - | DI | DI | NIS | -
Logical Exceptions
Loop No | Tag No | I/O Type | Voltage | IS/NIS | Location | To | Marshaling | idk | card | idk2 | card1 | card2 | channel | TB | all | system | real card | card-terminal | terminal-1 | terminal-2 | JB | terminal-1.1 | terminal-2.1 | SRC | IO_RAW | IO_KEY | SAFETY_RAW | LOC_RAW | Signal_Type | Rank_IO | Rank_Safety | Rank_Loc
II-700-88 | 0 | AI | 4-20 MA HART | NIS | MCC | DCS | DSC-001-001F | 13 | C1-AI12 | L1-12 | AI12 | - | 1 | TB1 | DSC-001-001F.C1-AI12.TB1 /DMC-001-004F.TB-C1-AI12 | DMC-001-004F | TB-C1-AI12 | - | 1A | 1B | MC-DM-IRP-700-011 | 1 | 2 | SC | AI | AI | NIS | MCC | ACTIVE | 1 | 2 | 2

## output_report
Global Metrics
Total Active Signals | 792
Actual Hot Spares | 162
Expected Hot Spares (approx 20%) | 159
Total Spare (Backfill) Channels | 70
Per Cabinet Statistics
Cabinet | Type | Direction | Limiting Factor | Rail Used (Max) | Barrier AI (Boards) | Barrier AO (Boards) | Barrier DI (Boards) | Barrier DO (Boards) | Terminal AI (Boards) | Terminal AO (Boards) | Terminal DI (Boards) | Terminal DO (Boards) | Relay AI (Boards) | Relay AO (Boards) | Relay DI (Boards) | Relay DO (Boards) | JB Count | Hot Spares | Backfill Spares
IS-A-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (100.0%) | 223 (800) | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9 | 9
IS-A-02R | Type 2 | REAR | PERCENT_PER_BOARD Pool (99.4%) | 358 (800) | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 26 | 0
IS-A-03F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (96.8%) | 350 (800) | 3 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 2
IS-A-04F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (34.2%) | 60 (800) | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 12
NIS-B-01R | Type 1 | REAR | PERCENT_PER_BOARD Pool (95.8%) | 180 (800) | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0 | 0 | 0 | 1 | 10 | 11 | 0
NIS-B-02F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | 252 (800) | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 3 | 0 | 14 | 20 | 0
NIS-B-03F | Type 1 | FRONT | PERCENT_PER_BOARD Pool (99.5%) | 256 (800) | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 3 | 0 | 16 | 18 | 0
NIS-B-04R | Type 2 | REAR | PERCENT_PER_BOARD Pool (97.2%) | 206 (800) | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 0 | 0 | 1 | 2 | 7 | 10 | 0
NIS-B-05F | Type 2 | FRONT | PERCENT_PER_BOARD Pool (93.6%) | 214 (800) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 0 | 3 | 0 | 11 | 18 | 0
NIS-B-06R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | 164 (800) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 2 | 12 | 11 | 10
NIS-B-07R | Type 3 | REAR | PERCENT_PER_BOARD Pool (100.0%) | 168 (800) | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 1 | 1 | 27 | 17 | 23
NIS-B-08F | Type 3 | FRONT | PERCENT_PER_BOARD Pool (28.4%) | 8 (800) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 14